## Legend
Dry coolers sizes
|  |  | L | lenght
|  |  | W | width
|  |  | H | height
Wet cooling towers sizes
| A | Height | H
| B | Width | W
| C | Depth | L

## Database
[8 empty] | Performance characteristics | [7 empty] | Fans´ characteristics | [7 empty] | Heat Exchanger type | [8 empty] | Costs
ID | Dry cooler | Hybrid cooler | Wet tower | L (or D) | W | H | Operating weight [kg] | refrigerated fluid | Refrigerated fluid rated volume flow rate m3/h | Refrigerated fluid rated temperature difference Tin-Tout °C | Rated cooling power [ kW] | Fluid -air rated temperature difference Tout-Tamb °C | Pressure drop [ kPa] | Rated air volume flow rate m3/h | Rated water consumption l/h | Number of fan rows | Fans number | Diameter | Y | Δ | Max electric power kW | Grid connection and control | Noise level dBA 10m | Surface m2 | Tubes volume (Di) dm3 | Aluminium | Copper | Epoxy | Other | Aluminium | Copper | Stainless steel | cooler cost euros or dollars (specify) | Wiring | EC controller | Water spray system | Switch board + inverter | Total cost | Spray system cost
1 | X |  |  | 880 | 990 | 980 | 48 | glycol (35%) - water | 3.3 | 5 | 17.2 | 10 | 41 | 7500 | _ | 1 | 1 | 500 | 980 | 1330 | 0.79 | 3 phase 400V/50Hz | 51 | 27 | 5 | X | X | X |  |  | X | X | 1611 | X | X |  |  | 2797
2 | X |  |  | 1660 | 900 | 980 | 90 | glycol (35%) - water | 6.2 | 5 | 32.4 | 10 | 15 | 15000 | _ | 1 | 2 | 500 | 980 | 1330 | 1.58 | 3 phase 400V/50Hz | 54 | 54 | 11 | X | X | X |  |  | X | X | 2258 | X | X |  |  | 3647
3 | X |  |  | 880 | 900 | 980 | 106 | glycol (35%) - water | 8.9 | 5 | 46.4 | 10 | 28 | 13000 | _ | 1 | 2 | 500 | 980 | 1330 | 1.58 | 3 phase 400V/50Hz | 54 | 108 | 22 | X | X | X |  |  | X | X | 2682 | X | X |  |  | 4071
4 | X |  |  | 1240 | 1260 | 980 | 79 | glycol (35%) - water | 6.7 | 5 | 35.2 | 10 | 20 | 16000 | _ | 1 | 1 | 630 | 1070 | 1340 | 1.9 | 3 phase 400V/50Hz | 58 | 58 | 12 | X | X | X |  |  | X | X | 2268 | X | X |  |  | 3454
5 | X |  |  | 2380 | 1260 | 980 | 151 | glycol (35%) - water | 14.2 | 5 | 74.6 | 10 | 48 | 32000 | _ | 1 | 2 | 630 | 1070 | 1340 | 3.8 | 3 phase 400V/50Hz | 60 | 115 | 24 | X | X | X |  |  | X | X | 3608 | X | X |  |  | 4997
6 | X |  |  | 3520 | 2260 | 980 | 248 | glycol (35%) - water | 27.3 | 5 | 143 | 10 | 102 | 45000 | _ | 1 | 3 | 630 | 1070 | 1340 | 5.7 | 3 phase 400V/50Hz | 62 | 259 | 51 | X | X | X |  |  | X | X | 5543 | X | X |  |  | 7134
7 | X |  |  | 4660 | 1260 | 980 | 362 | glycol (35%) - water | 38.2 | 5 | 199.9 | 10 | 22 | 56800 | _ | 1 | 4 | 630 | 1070 | 1340 | 7.6 | 3 phase 400V/50Hz | 63 | 460 | 89 | X | X | X |  |  | X | X | 7893 | X | X |  |  | 9685
8 | X |  |  | 1470 | 1380 | 1565 | 146 | glycol (35%) - water | 9.1 | 5 | 47.6 | 10 | 35 | 20700 | _ | 1 | 1 | 800 | 685 | 895 | 1.2 | 3 phase 400V/50Hz | 48 | 76 | 16 | X | X | X |  |  | X | X | 3580 | X | X |  |  | 4766
9 | X |  |  | 2820 | 1380 | 1565 | 280 | glycol (35%) - water | 18.9 | 5 | 99.3 | 10 | 77 | 41400 | _ | 1 | 2 | 800 | 685 | 895 | 2.4 | 3 phase 400V/50Hz | 51 | 151 | 30 | X | X | X |  |  | X | X | 5365 | X | X |  |  | 6754
10 | X |  |  | 4170 | 1380 | 1565 | 449 | glycol (35%) - water | 33 | 5 | 172.7 | 10 | 21 | 57900 | _ | 1 | 3 | 800 | 685 | 895 | 3.6 | 3 phase 400V/50Hz | 53 | 339 | 69 | X | X | X |  |  | X | X | 8633 | X | X |  |  | 10224
11 | X |  |  | 5520 | 1380 | 1565 | 642 | glycol (35%) - water | 49.6 | 5 | 259.9 | 10 | 35 | 71600 | _ | 1 | 4 | 800 | 685 | 895 | 4.8 | 3 phase 400V/50Hz | 54 | 602 | 114 | X | X | X |  |  | X | X | 12048 | X | X |  |  | 13840
12 | X |  |  | 6870 | 1380 | 1565 | 894 | glycol (35%) - water | 60.6 | 5 | 317.7 | 10 | 28 | 89500 | _ | 1 | 5 | 800 | 685 | 895 | 6 | 3 phase 400V/50Hz | 55 | 1054 | 174 | X | X | X |  |  | X | X | 15079 | X | X |  |  | 17156
13 | X |  |  | 8220 | 1380 | 1565 | 1039 | glycol (35%) - water | 74.5 | 5 | 390.2 | 10 | 49 | 107400 | _ | 1 | 6 | 800 | 685 | 895 | 7.2 | 3 phase 400V/50Hz | 56 | 1265 | 215 | X | X | X |  |  | X | X | 17952 | X | X |  |  | 20230
14 | X |  |  | 9570 | 1380 | 1565 | 1210 | glycol (35%) - water | 88.3 | 5 | 462.8 | 10 | 76 | 125300 | _ | 1 | 7 | 800 | 685 | 895 | 8.4 | 3 phase 400V/50Hz | 56 | 1476 | 248 | X | X | X |  |  | X | X | 20432 | X | X |  |  | 22913
15 | X |  |  | 1470 | 2400 | 1565 | 243 | glycol (35%) - water | 17.2 | 5 | 90.2 | 10 | 40 | 40200 | _ | 2 | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 137 | 32 | X | X | X |  |  | X | X | 5523 | X | X |  |  | 7568
16 | X |  |  | 2820 | 2400 | 1565 | 463 | glycol (35%) - water | 34.2 | 5 | 179.3 | 10 | 34 | 80400 | _ | 2 | 4 | 800 | 685 | 895 | 8 | 3 phase 400V/50Hz | 54 | 273 | 60 | X | X | X |  |  | X | X | 8763 | X | X |  |  | 11213
17 | X |  |  | 4170 | 2400 | 1565 | 691 | glycol (35%) - water | 51.3 | 5 | 268.9 | 10 | 33 | 120600 | _ | 2 | 6 | 800 | 685 | 895 | 12 | 3 phase 400V/50Hz | 56 | 409 | 89 | X | X | X |  |  | X | X | 12612 | X | X |  |  | 15548
18 | X |  |  | 5520 | 2400 | 1565 | 914 | glycol (35%) - water | 71.6 | 5 | 375 | 10 | 79 | 160800 | _ | 2 | 8 | 800 | 685 | 895 | 16 | 3 phase 400V/50Hz | 57 | 545 | 112 | X | X | X |  |  | X | X | 15880 | X | X |  |  | 19360
19 | X |  |  | 5520 | 2400 | 1565 | 987 | glycol (35%) - water | 86.5 | 5 | 453 | 10 | 54 | 148000 | _ | 2 | 8 | 800 | 685 | 895 | 16 | 3 phase 400V/50Hz | 57 | 817 | 175 | X | X | X |  |  | X | X | 18608 | X | X |  |  | 22088
20 | X |  |  | 6870 | 2400 | 1565 | 1340 | glycol (35%) - water | 104.7 | 5 | 548.6 | 10 | 44 | 185000 | _ | 2 | 10 | 800 | 685 | 895 | 20 | 3 phase 400V/50Hz | 58 | 1423 | 255 | X | X | X |  |  | X | X | 22956 | X | X |  |  | 27846
21 | X |  |  | 8220 | 2400 | 1565 | 1581 | glycol (35%) - water | 128.9 | 5 | 675.2 | 10 | 75 | 222000 | _ | 2 | 12 | 800 | 685 | 895 | 24 | 3 phase 400V/50Hz | 58 | 1707 | 299 | X | X | X |  |  | X | X | 26881 | X | X |  |  | 31771
22 | X |  |  | 9570 | 2400 | 1565 | 1841 | glycol (35%) - water | 153 | 5 | 801.8 | 10 | 118 | 259000 | _ | 2 | 14 | 800 | 685 | 895 | 28 | 3 phase 400V/50Hz | 58 | 1992 | 343 | X | X | X |  |  | X | X | 30670 | X | X |  |  | 35963
23 | X |  |  | 10920 | 2400 | 1565 | 2318 | glycol (35%) - water | 193 | 5 | 1011.3 | 10 | 122 | 275200 | _ | 2 | 16 | 800 | 685 | 895 | 32 | 3 phase 400V/50Hz | 59 | 3035 | 505 | X | X | X |  |  | X | X | 39307 | X | X |  |  | 45005
24 | X |  |  | 1620 | 2400 | 1565 | 294 | glycol (35%) - water | 22.6 | 5 | 118.6 | 10 | 71 | 57400 | _ | 2 | 2 | 900 | 716 | 893 | 7.2 | 3 phase 400V/50Hz | 59 | 152 | 39 | X | X | X |  |  | X | X | 6585 | X | X |  |  | 8662
25 | X |  |  | 3120 | 2400 | 1565 | 562 | glycol (35%) - water | 41.3 | 5 | 216.6 | 10 | 17 | 114800 | _ | 2 | 4 | 900 | 716 | 893 | 14.4 | 3 phase 400V/50Hz | 62 | 303 | 71 | X | X | X |  |  | X | X | 10610 | X | X |  |  | 13314
26 | X |  |  | 3120 | 2400 | 1565 | 656 | glycol (35%) - water | 61 | 5 | 319.6 | 10 | 69 | 92400 | _ | 2 | 4 | 900 | 716 | 893 | 14.4 | 3 phase 400V/50Hz | 62 | 605 | 123 | X | X | X |  |  | X | X | 13429 | X | X |  |  | 16133
27 | X |  |  | 4620 | 2400 | 1565 | 901 | glycol (35%) - water | 82 | 5 | 429.6 | 10 | 41 | 154800 | _ | 2 | 6 | 900 | 716 | 893 | 21.6 | 3 phase 400V/50Hz | 64 | 681 | 151 | X | X | X |  |  | X | X | 17500 | X | X |  |  | 21209
28 | X |  |  | 6120 | 2400 | 1565 | 1293 | glycol (35%) - water | 105.4 | 5 | 552.4 | 10 | 39 | 206400 | _ | 2 | 8 | 900 | 716 | 893 | 28.8 | 3 phase 400V/50Hz | 65 | 1265 | 231 | X | X | X |  |  | X | X | 22724 | X | X |  |  | 26838
29 | X |  |  | 7620 | 2400 | 1565 | 1589 | glycol (35%) - water | 136.5 | 5 | 715.1 | 10 | 77 | 258000 | _ | 2 | 10 | 900 | 716 | 893 | 36 | 3 phase 400V/50Hz | 65 | 1581 | 280 | X | X | X |  |  | X | X | 27674 | X | X |  |  | 31859
30 | X |  |  | 9120 | 2400 | 1565 | 1902 | glycol (35%) - water | 181 | 5 | 948.7 | 10 | 91 | 240000 | _ | 2 | 12 | 900 | 716 | 893 | 43.2 | 3 phase 400V/50Hz | _ | 2529 | 329 | X | X | X |  |  | X | X | 36511 | X | X |  |  | 42301
31 | X |  |  | 10620 | 2400 | 1565 | 2426 | glycol (35%) - water | 214.5 | 5 | 1123.9 | 10 | 143 | 323400 | _ | 2 | 14 | 900 | 716 | 893 | 50.4 | 3 phase 400V/50Hz | 66 | 2951 | 492 | X | X | X |  |  | X | X | 41847 | X | X |  |  | 48042
32 | X |  |  | 4320 | 1181 | 1804 | 744 | glycol (35%) - water | 48.6 | 5 | 254.6 | 10 | 26 | 101400 | _ | 1 | 3 | 900 | 716 | 893 | 10.8 | 3 phase 400V/50Hz | 61 | 468 | 95 | X |  |  |  |  | X |  | 13983 | X | X |  |  | 15655
33 | X |  |  | 5720 | 1181 | 1804 | 1058 | glycol (35%) - water | 82 | 5 | 429.9 | 10 | 43 | 129600 | _ | 1 | 4 | 900 | 716 | 893 | 14.4 | 3 phase 400V/50Hz | 62 | 936 | 175 | X |  |  |  |  | X |  | 20190 | X | X |  |  | 22065
34 | X |  |  | 7120 | 1181 | 1804 | 1583 | glycol (35%) - water | 111.1 | 5 | 582.7 | 10 | 25 | 156500 | _ | 1 | 5 | 900 | 716 | 893 | 18 | 3 phase 400V/50Hz | 63 | 2186 | 378 | X |  |  |  |  | X |  | 29624 | X | X |  |  | 31701
35 | X |  |  | 8520 | 1181 | 1804 | 1878 | glycol (35%) - water | 136.3 | 5 | 714.6 | 10 | 43 | 187800 | _ | 1 | 6 | 900 | 716 | 893 | 21.6 | 3 phase 400V/50Hz | 63 | 2623 | 445 | X |  |  |  |  | X |  | 34486 | X | X |  |  | 37365
36 | X |  |  | 9920 | 1181 | 1804 | 2173 | glycol (35%) - water | 161.4 | 5 | 846.3 | 10 | 68 | 219100 | _ | 1 | 7 | 900 | 716 | 893 | 25.2 | 3 phase 400V/50Hz | 63 | 3060 | 513 | X |  |  |  |  | X |  | 39308 | X | X |  |  | 42390
37 | X |  |  | 4044 | 1181 | 1804 | 700 | glycol (35%) - water | 33.1 | 5 | 173.4 | 10 | 24 | 65937 | _ | 1 | 2 | 900 | 716 | 893 | 7.2 | 3 phase 400V/50Hz | 59 | 648 | 54 | X |  |  |  |  | X |  | 11230 | X | X |  |  | 12684
38 | X |  |  | 6004 | 1181 | 1804 | 983 | glycol (35%) - water | 52.7 | 5 | 276.3 | 10 | 81 | 98906 | _ | 1 | 3 | 900 | 716 | 893 | 10.8 | 3 phase 400V/50Hz | 61 | 971 | 80 | X |  |  |  |  | X |  | 14534 | X | X |  |  | 16271
39 | X |  |  | 7964 | 1181 | 1804 | 1332 | glycol (35%) - water | 74.5 | 5 | 390.4 | 10 | 47 | 130915 | _ | 1 | 4 | 900 | 716 | 893 | 14.4 | 3 phase 400V/50Hz | 62 | 1224 | 187 | X |  |  |  |  | X |  | 19794 | X | X |  |  | 21734
40 | X |  |  | 9924 | 1181 | 1804 | 1630 | glycol (35%) - water | 95.5 | 5 | 500.5 | 10 | 91 | 163643 | _ | 1 | 5 | 900 | 716 | 893 | 18 | 3 phase 400V/50Hz | 62 | 1530 | 234 | X |  |  |  |  | X |  | 23522 | X | X |  |  | 25664
41 | X |  |  | 9924 | 1181 | 1804 | 2074 | glycol (35%) - water | 124.1 | 5 | 650.6 | 10 | 42 | 157390 | _ | 1 | 5 | 900 | 716 | 893 | 18 | 3 phase 400V/50Hz | 62 | 3060 | 468 | X |  |  |  |  | X |  | 34415 | X | X |  |  | 36557
42 | X |  |  | 2920 | 1181 | 1804 | 527 | glycol (35%) - water | 33.8 | 5 | 177.3 | 10 | 65 | 67600 | _ | 1 | 2 | 900 | 716 | 893 | 7.2 | 3 phase 400V/50Hz | 59 | 312 | 63 | X |  |  |  |  | X |  | 9994 | X | X |  |  | 11383
43 | X |  |  | 2680 | 2410 | 2262 | 1074 | glycol (35%) - water | 52 | 5 | 272.7 | 10 | 29 | 125200 | _ | 2 | 4 | 900 | 716 | 893 | 14.4 | 3 phase 400V/50Hz | 62 | 411 | 92 | X |  |  |  |  | X |  | 16339 | X | X |  |  | 19011
44 | X |  |  | 3930 | 2410 | 2262 | 1492 | glycol (35%) - water | 77.8 | 5 | 407.9 | 10 | 27 | 187800 | _ | 2 | 6 | 900 | 716 | 893 | 21.6 | 3 phase 400V/50Hz | 64 | 617 | 137 | X |  |  |  |  | X |  | 22443 | X | X |  |  | 26119
45 | X |  |  | 5180 | 2410 | 2262 | 2151 | glycol (35%) - water | 123.8 | 5 | 648.4 | 10 | 19 | 235200 | _ | 2 | 8 | 900 | 716 | 893 | 28.8 | 3 phase 400V/50Hz | 65 | 1717 | 323 | X |  |  |  |  | X |  | 33243 | X | X |  |  | 37324
46 | X |  |  | 6430 | 2410 | 2262 | 2638 | glycol (35%) - water | 161.4 | 5 | 845.7 | 10 | 37 | 294000 | _ | 2 | 10 | 900 | 716 | 893 | 36 | 3 phase 400V/50Hz | 65 | 2147 | 390 | X |  |  |  |  | X |  | 40093 | X | X |  |  | 44246
47 | X |  |  | 7680 | 2410 | 2262 | 3356 | glycol (35%) - water | 219.8 | 5 | 1151.8 | 10 | 46 | 331200 | _ | 2 | 12 | 900 | 716 | 893 | 43.2 | 3 phase 400V/50Hz | 66 | 3434 | 589 | X |  |  |  |  | X |  | 52274 | X | X |  |  | 58032
48 | X |  |  | 10182 | 2410 | 2262 | 2173 | glycol (35%) - water | 302.5 | 5 | 1585 | 10 | 106 | 441600 | _ | 2 | 16 | 900 | 716 | 893 | 57.6 | 3 phase 400V/50Hz | 63 | 4579 | 513 | X |  |  |  |  | X |  | 67050 | X | X |  |  | 73616
49 | X |  |  | 4182 | 2410 | 2262 | 1204 | glycol (35%) - water | 58.3 | 5 | 305.4 | 10 | 34 | 129095 | _ | 2 | 4 | 900 | 716 | 893 | 14.4 | 3 phase 400V/50Hz | 62 | 969 | 80 | X |  |  |  |  | X |  | 17840 | X | X |  |  | 20609
50 | X |  |  | 6182 | 2410 | 2262 | 1765 | glycol (35%) - water | 95.3 | 5 | 499.2 | 10 | 28 | 191445 | _ | 2 | 6 | 900 | 716 | 893 | 21.6 | 3 phase 400V/50Hz | 63 | 1374 | 210 | X |  |  |  |  | X |  | 26052 | X | X |  |  | 29825
51 | X |  |  | 8182 | 2410 | 2262 | 2275 | glycol (35%) - water | 132.7 | 5 | 695.2 | 10 | 68 | 255259 | _ | 2 | 8 | 900 | 716 | 893 | 28.8 | 3 phase 400V/50Hz | 64 | 1832 | 280 | X |  |  |  |  | X |  | 32679 | X | X |  |  | 36857
52 | X |  |  | 10182 | 2410 | 2262 | 3118 | glycol (35%) - water | 206.6 | 5 | 1082.6 | 10 | 90 | 310358 | _ | 2 | 10 | 900 | 716 | 893 | 36 | 3 phase 400V/50Hz | 65 | 3435 | 525 | X |  |  |  |  | X |  | 47798 | X | X |  |  | 52048
53 | X |  |  | 2940 | 2230 | 2210 | 585 | Water | 38.7 | 5 | 222.3 | 10 | 71.9 | 88780 | _ |  | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 636.5 | 55.4 | X |  |  | AlMg |  | X | X | 6421 |  | X |  | X | 15801
54 | X |  |  | 2940 | 2230 | 2210 | 675 | Water | 47.6 | 5 | 273.9 | 10 | 30.7 | 86052 | _ |  | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 954.68 | 83.2 | X |  |  | AlMg |  | X | X | 7070 |  | X |  | X | 16450
55 | X |  |  | 2940 | 2230 | 2210 | 774 | Water | 54.1 | 5 | 310.9 | 10 | 51 | 83370 | _ |  | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 1272.86 | 110.9 | X |  |  | AlMg |  | X | X | 7916 |  | X |  | X | 17296
56 | X |  |  | 4250 | 2230 | 2210 | 765 | Water | 57.9 | 5 | 333.2 | 10 | 58.2 | 133258 | _ |  | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 960.92 | 83.7 | X |  |  | AlMg |  | X | X | 8660 |  | X |  | X | 20579
57 | X |  |  | 4250 | 2230 | 2210 | 945 | Water | 72.2 | 5 | 415 | 10 | 42 | 129210 | _ |  | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1441.24 | 125.5 | X |  |  | AlMg |  | X | X | 9591 |  | X |  | X | 21510
58 | X |  |  | 4250 | 2230 | 2210 | 1125 | Water | 81.7 | 5 | 469.9 | 10 | 69.5 | 125227 | _ |  | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1921.7 | 167.4 | X |  |  | AlMg |  | X | X | 11086 |  | X |  | X | 23005
59 | X |  |  | 5560 | 2230 | 2210 | 1152 | Water | 77.9 | 5 | 448 | 10 | 80.2 | 177736 | _ |  | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1285.33 | 111.9 | X |  |  | AlMg |  | X | X | 11138 |  | X |  | X | 26526
60 | X |  |  | 5560 | 2230 | 2210 | 1332 | Water | 96.9 | 5 | 557 | 10 | 55.1 | 172368 | _ |  | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1927.93 | 167.9 | X |  |  | AlMg |  | X | X | 12134 |  | X |  | X | 27522
61 | X |  |  | 5560 | 2230 | 2210 | 1530 | Water | 109.1 | 5 | 627.4 | 10 | 68.6 | 167083 | _ |  | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 2570.53 | 223.9 | X |  |  | AlMg |  | X | X | 14010 |  | X |  | X | 29398
62 | X |  |  | 6870 | 2230 | 2210 | 1440 | Water | 97.4 | 5 | 560.1 | 10 | 77.2 | 222214 | _ |  | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 1609.61 | 140.2 | X |  |  | AlMg |  | X | X | 13391 |  | X |  | X | 32288
63 | X |  |  | 6870 | 2230 | 2210 | 1665 | Water | 121.2 | 5 | 697.1 | 10 | 55.7 | 215525 | _ |  | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 2414.49 | 210.3 | X |  |  | AlMg |  | X | X | 14635 |  | X |  | X | 33532
64 | X |  |  | 6870 | 2230 | 2210 | 1913 | Water | 136.9 | 5 | 787.1 | 10 | 84.9 | 208939 | _ |  | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 3219.36 | 280.4 | X |  |  | AlMg |  | X | X | 17123 |  | X |  | X | 36020
65 | X |  |  | 8190 | 2230 | 2210 | 1620 | Water | 112.8 | 5 | 648.4 | 10 | 17.4 | 266691 | _ |  | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 1934.03 | 168.5 | X |  |  | AlMg |  | X | X | 15641 |  | X |  | X | 37897
66 | X |  |  | 8190 | 2230 | 2210 | 1890 | Water | 140.7 | 5 | 809.2 | 10 | 12.6 | 258681 | _ |  | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 2901.18 | 252.7 | X |  |  | AlMg |  | X | X | 17136 |  | X |  | X | 39392
67 | X |  |  | 8190 | 2230 | 2210 | 2250 | Water | 163.9 | 5 | 942.2 | 10 | 67.7 | 250794 | _ |  | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 3868.2 | 336.9 | X |  |  | AlMg |  | X | X | 20121 |  | X |  | X | 42377
68 | X |  |  | 9430 | 2230 | 2210 | 2070 | Water | 133.3 | 5 | 766.6 | 10 | 27.2 | 311169 | _ |  | 14 | 800 | 660 | 880 | 28 | 3 phase 400V/50Hz | 61 | 2258.45 | 196.7 | X |  |  | AlMg |  | X | X | _
69 | X |  |  | 9490 | 2230 | 2210 | 2340 | Water | 166.2 | 5 | 955.7 | 10 | 19.7 | 301838 | _ |  | 14 | 800 | 660 | 880 | 28 | 3 phase 400V/50Hz | 61 | 3387.74 | 295.1 | X |  |  | AlMg |  | X | X | _
70 | X |  |  | 9490 | 2230 | 2210 | 2691 | Water | 186.1 | 5 | 1069.9 | 10 | 14.4 | 292649 | _ |  | 14 | 800 | 660 | 880 | 28 | 3 phase 400V/50Hz | 61 | 4517.03 | 393.4 | X |  |  | AlMg |  | X | X | _
71 | X |  |  | 10800 | 2230 | 2210 | 2430 | Water | 153.9 | 5 | 885 | 10 | 40 | 355646 | _ |  | 16 | 800 | 660 | 880 | 32 | 3 phase 400V/50Hz | 62 | 2582.86 | 225 | X |  |  | AlMg |  | X | X | _
72 | X |  |  | 10800 | 2230 | 2210 | 2682 | Water | 191.7 | 5 | 1102.4 | 10 | 28.9 | 344995 | _ |  | 16 | 800 | 660 | 880 | 32 | 3 phase 400V/50Hz | 62 | 3874.43 | 337.5 | X |  |  | AlMg |  | X | X | _
73 | X |  |  | 10800 | 2230 | 2210 | 3042 | Water | 214.5 | 5 | 1233.5 | 10 | 21.2 | 334504 | _ |  | 16 | 800 | 660 | 880 | 32 | 3 phase 400V/50Hz | 62 | 5165.86 | 450 | X |  |  | AlMg |  | X | X | _
74 | X |  |  | 2940 | 2230 | 2210 | 585 | Water | 38.4 | 5 | 221 | 10 | 42.8 | 89655 | _ |  | 4 | 910 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 636.5 | 55.4 | X |  |  | AlMg |  | X | X | 7076 |  | X |  | X | 16045
75 | X |  |  | 2940 | 2230 | 2210 | 675 | Water | 48.6 | 5 | 279.2 | 10 | 63.8 | 86693 | _ |  | 4 | 910 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 954.68 | 83.2 | X |  |  | AlMg |  | X | X | 7624 |  | X |  | X | 16593
76 | X |  |  | 2940 | 2230 | 2210 | 774 | Water | 54.2 | 5 | 311.9 | 10 | 51.3 | 83717 | _ |  | 4 | 910 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 1272.86 | 110.9 | X |  |  | AlMg |  | X | X | 8720 |  | X |  | X | 17689
77 | X |  |  | 4250 | 2230 | 2210 | 765 | Water | 58.3 | 5 | 335.1 | 10 | 58.8 | 134577 | _ |  | 6 | 910 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 960.92 | 83.7 | X |  |  | AlMg |  | X | X | 9607 |  | X |  | X | 20908
78 | X |  |  | 4250 | 2230 | 2210 | 945 | Water | 72.5 | 5 | 417 | 10 | 42.4 | 130186 | _ |  | 6 | 910 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1441.24 | 125.5 | X |  |  | AlMg |  | X | X | 10568 |  | X |  | X | 21869
79 | X |  |  | 4250 | 2230 | 2210 | 1125 | Water | 82 | 5 | 471.4 | 10 | 70 | 125767 | _ |  | 6 | 910 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1921.7 | 167.4 | X |  |  | AlMg |  | X | X | 12212 |  | X |  | X | 23513
80 | X |  |  | 5560 | 2230 | 2210 | 1152 | Water | 77.2 | 5 | 444 | 10 | 41.2 | 179499 | _ |  | 8 | 910 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1285.33 | 111.9 | X |  |  | AlMg |  | X | X | 12273 |  | X |  | X | 26739
81 | X |  |  | 5560 | 2230 | 2210 | 1332 | Water | 97.4 | 5 | 559.8 | 10 | 55.6 | 173678 | _ |  | 8 | 910 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1927.93 | 167.9 | X |  |  | AlMg |  | X | X | 13370 |  | X |  | X | 27836
82 | X |  |  | 5560 | 2230 | 2210 | 1530 | Water | 108.8 | 5 | 625.6 | 10 | 45.7 | 167816 | _ |  | 8 | 910 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 2570.53 | 223.9 | X |  |  | AlMg |  | X | X | 15562 |  | X |  | X | 30028
83 | X |  |  | 6870 | 2230 | 2210 | 1440 | Water | 98 | 5 | 563.3 | 10 | 78 | 224420 | _ |  | 10 | 910 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 1609.61 | 140.2 | X |  |  | AlMg |  | X | X | 14755 |  | X |  | X | 32526
84 | X |  |  | 6870 | 2230 | 2210 | 1665 | Water | 121.8 | 5 | 700.6 | 10 | 56.2 | 217169 | _ |  | 10 | 910 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 2414.49 | 210.3 | X |  |  | AlMg |  | X | X | 16125 |  | X |  | X | 33896
85 | X |  |  | 6870 | 2230 | 2210 | 1913 | Water | 135.9 | 5 | 781.3 | 10 | 40.8 | 209865 | _ |  | 10 | 910 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 3219.36 | 280.4 | X |  |  | AlMg |  | X | X | 18865 |  | X |  | X | 36636
86 | X |  |  | 8190 | 2230 | 2210 | 1620 | Water | 113.4 | 5 | 652.1 | 10 | 17.5 | 269340 | _ |  | 12 | 910 | 660 | 860 | 19.8 | 3 phase 400V/50Hz | 63 | 1934.03 | 168.5 | X |  |  | AlMg |  | X | X | _
87 | X |  |  | 8190 | 2230 | 2210 | 1890 | Water | 141.3 | 5 | 812.4 | 10 | 12.6 | 260660 | _ |  | 12 | 910 | 660 | 860 | 19.8 | 3 phase 400V/50Hz | 63 | 2901.18 | 252.7 | X |  |  | AlMg |  | X | X | _
88 | X |  |  | 8190 | 2230 | 2210 | 2250 | Water | 164.4 | 5 | 945.4 | 10 | 68.1 | 251913 | _ |  | 12 | 910 | 660 | 860 | 19.8 | 3 phase 400V/50Hz | 63 | 3868.2 | 336.9 | X |  |  | AlMg |  | X | X | _
89 | X |  |  | 9490 | 2230 | 2210 | 2070 | Water | 134.1 | 5 | 770.9 | 10 | 27.5 | 314261 | _ |  | 14 | 910 | 660 | 860 | 23.1 | 3 phase 400V/50Hz | 63 | 2258.45 | 196.7 | X |  |  | AlMg |  | X | X | _
90 | X |  |  | 9490 | 2230 | 2210 | 2340 | Water | 167.1 | 5 | 960.6 | 10 | 19.9 | 304151 | _ |  | 14 | 910 | 660 | 860 | 23.1 | 3 phase 400V/50Hz | 63 | 3387.74 | 295.1 | X |  |  | AlMg |  | X | X | _
91 | X |  |  | 9490 | 2230 | 2210 | 2691 | Water | 186.7 | 5 | 1073.4 | 10 | 14.5 | 293961 | _ |  | 14 | 910 | 660 | 860 | 23.1 | 3 phase 400V/50Hz | 63 | 4517.03 | 393.4 | X |  |  | AlMg |  | X | X | _
92 | X |  |  | 10800 | 2230 | 2210 | 2430 | Water | 154.8 | 5 | 890 | 10 | 40.4 | 359182 | _ |  | 16 | 910 | 660 | 860 | 26.4 | 3 phase 400V/50Hz | 64 | 2582.86 | 225 | X |  |  | AlMg |  | X | X | _
93 | X |  |  | 10800 | 2230 | 2210 | 2682 | Water | 192.7 | 5 | 1108 | 10 | 29.2 | 347642 | _ |  | 16 | 910 | 660 | 860 | 26.4 | 3 phase 400V/50Hz | 64 | 3874.43 | 337.5 | X |  |  | AlMg |  | X | X | _
94 | X |  |  | 10800 | 2230 | 2210 | 3042 | Water | 215.3 | 5 | 1237.8 | 10 | 21.4 | 336009 | _ |  | 16 | 910 | 660 | 860 | 26.4 | 3 phase 400V/50Hz | 64 | 5165.86 | 450 | X |  |  | AlMg |  | X | X | _
95 | X |  |  | 2940 | 2230 | 2210 | 690 | Water | 34.7 | 5 | 199.4 | 10 | 15.1 | 87993 | _ |  | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 597.5 | 97.6 | X |  |  | AlMg |  | X | X | _
96 | X |  |  | 2940 | 2230 | 2210 | 797 | Water | 43.8 | 5 | 251.9 | 10 | 13.4 | 84884 | _ |  | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 895.5 | 146.6 | X |  |  | AlMg |  | X | X | _
97 | X |  |  | 2940 | 2230 | 2210 | 913 | Water | 49.5 | 5 | 284.6 | 10 | 11.1 | 81868 | _ |  | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 1194.1 | 195.4 | X |  |  | AlMg |  | X | X | _
98 | X |  |  | 4250 | 2230 | 2210 | 903 | Water | 54 | 5 | 310.3 | 10 | 48 | 132092 | _ |  | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 901.3 | 147.5 | X |  |  | AlMg |  | X | X | _
99 | X |  |  | 4250 | 2230 | 2210 | 1115 | Water | 68 | 5 | 390.8 | 10 | 42.9 | 127476 | _ |  | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1352.1 | 221.1 | X |  |  | AlMg |  | X | X | _
100 | X |  |  | 4250 | 2230 | 2210 | 1328 | Water | 76.5 | 5 | 440 | 10 | 35.2 | 122995 | _ |  | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1802.8 | 294.9 | X |  |  | AlMg |  | X | X | _
101 | X |  |  | 5560 | 2230 | 2210 | 1359 | Water | 71.1 | 5 | 408.7 | 10 | 27.9 | 176190 | _ |  | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1205.7 | 197.1 | X |  |  | AlMg |  | X | X | _
102 | X |  |  | 5560 | 2230 | 2210 | 1572 | Water | 90.9 | 5 | 522.8 | 10 | 47 | 170067 | _ |  | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1808.5 | 295.8 | X |  |  | AlMg |  | X | X | _
103 | X |  |  | 6870 | 2230 | 2210 | 1805 | Water | 102.1 | 5 | 587.4 | 10 | 34.7 | 164119 | _ |  | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 2411.4 | 394.4 | X |  |  | AlMg |  | X | X | _
104 | X |  |  | 6870 | 2230 | 2210 | 1699 | Water | 89.3 | 5 | 513.3 | 10 | 32.1 | 220287 | _ |  | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 1510 | 247 | X |  |  | AlMg |  | X | X | _
105 | X |  |  | 6870 | 2230 | 2210 | 1965 | Water | 113.3 | 5 | 651.5 | 10 | 38.7 | 212658 | _ |  | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 2265 | 370.5 | X |  |  | AlMg |  | X | X | _
106 | X |  |  | 6870 | 2230 | 2210 | 2257 | Water | 127.3 | 5 | 732.2 | 10 | 28.7 | 205244 | _ |  | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 3020 | 494 | X |  |  | AlMg |  | X | X | _
107 | X |  |  | 8190 | 2230 | 2210 | 1912 | Water | 106.7 | 5 | 613.7 | 10 | 27.5 | 264384 | _ |  | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 1814.3 | 296.8 | X |  |  | AlMg |  | X | X | _
108 | X |  |  | 8190 | 2230 | 2210 | 2230 | Water | 136 | 5 | 781.8 | 10 | 37.7 | 255248 | _ |  | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 2721.6 | 445.2 | X |  |  | AlMg |  | X | X | _
109 | X |  |  | 8190 | 2230 | 2210 | 2655 | Water | 153.2 | 5 | 880.8 | 10 | 31.7 | 246368 | _ |  | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 3628.73 | 593.5 | X |  |  | AlMg |  | X | X | _
110 | X |  |  | 9490 | 2230 | 2210 | 2443 | Water | 126.1 | 5 | 724.8 | 10 | 42.9 | 308481 | _ |  | 14 | 800 | 660 | 880 | 28 | 3 phase 400V/50Hz | 61 | 2118.7 | 346.5 | X |  |  | AlMg |  | X | X | _
111 | X |  |  | 9490 | 2230 | 2210 | 2761 | Water | 157.9 | 5 | 907.9 | 10 | 31.2 | 297839 | _ |  | 14 | 800 | 660 | 880 | 28 | 3 phase 400V/50Hz | 61 | 3178 | 519.9 | X |  |  | AlMg |  | X | X | _
112 | X |  |  | 9490 | 2230 | 2210 | 3175 | Water | 180.2 | 5 | 1036 | 10 | 49 | 287492 | _ |  | 14 | 800 | 660 | 880 | 28 | 3 phase 400V/50Hz | 61 | 4237.4 | 693.1 | X |  |  | AlMg |  | X | X | _
113 | X |  |  | 10800 | 2230 | 2210 | 2867 | Water | 145.4 | 5 | 836.1 | 10 | 63 | 352578 | _ |  | 16 | 800 | 660 | 880 | 32 | 3 phase 400V/50Hz | 62 | 2423 | 396.4 | X |  |  | AlMg |  | X | X | _
114 | X |  |  | 10800 | 2230 | 2210 | 3165 | Water | 182.2 | 5 | 1047.5 | 10 | 46 | 340429 | _ |  | 16 | 800 | 660 | 880 | 32 | 3 phase 400V/50Hz | 62 | 3634.5 | 594.6 | X |  |  | AlMg |  | X | X | _
115 | X |  |  | 10800 | 2230 | 2210 | 3590 | Water | 204.7 | 5 | 1176.8 | 10 | 34 | 328616 | _ |  | 16 | 800 | 660 | 880 | 32 | 3 phase 400V/50Hz | 62 | 4846 | 792.8 | X |  |  | AlMg |  | X | X | _
116 | X |  |  | 2940 | 2230 | 2210 | 690 | Water | 34.9 | 5 | 200.5 | 10 | 15.2 | 88812 | _ |  | 4 | 910 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 597.5 | 97.6 | X |  |  | AlMg |  | X | X | _
117 | X |  |  | 2940 | 2230 | 2210 | 797 | Water | 44 | 5 | 252.9 | 10 | 13.5 | 85402 | _ |  | 4 | 910 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 895.5 | 146.6 | X |  |  | AlMg |  | X | X | _
118 | X |  |  | 2940 | 2230 | 2210 | 913 | Water | 49.6 | 5 | 285 | 10 | 11.1 | 82038 | _ |  | 4 | 910 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 1194.1 | 195.4 | X |  |  | AlMg |  | X | X | _
119 | X |  |  | 4250 | 2230 | 2210 | 903 | Water | 53.5 | 5 | 307.8 | 10 | 28.5 | 133328 | _ |  | 6 | 910 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 901.3 | 147.5 | X |  |  | AlMg |  | X | X | _
120 | X |  |  | 4250 | 2230 | 2210 | 1115 | Water | 68.3 | 5 | 392.4 | 10 | 43.2 | 128271 | _ |  | 6 | 910 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1352.1 | 221.1 | X |  |  | AlMg |  | X | X | _
121 | X |  |  | 4250 | 2230 | 2210 | 1328 | Water | 76.6 | 5 | 440.7 | 10 | 35.3 | 123272 | _ |  | 6 | 910 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1802.8 | 294.9 | X |  |  | AlMg |  | X | X | _
122 | X |  |  | 5560 | 2230 | 2210 | 1359 | Water | 71.5 | 5 | 411 | 10 | 28.2 | 177843 | _ |  | 8 | 910 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1205.7 | 197.1 | X |  |  | AlMg |  | X | X | _
123 | X |  |  | 5560 | 2230 | 2210 | 1572 | Water | 89.5 | 5 | 514.5 | 10 | 20.4 | 171137 | _ |  | 8 | 910 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1808.5 | 295.8 | X |  |  | AlMg |  | X | X | _
124 | X |  |  | 5560 | 2230 | 2210 | 1805 | Water | 102.3 | 5 | 588.4 | 10 | 34.9 | 164504 | _ |  | 8 | 910 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 2411.4 | 394.4 | X |  |  | AlMg |  | X | X | _
125 | X |  |  | 6870 | 2230 | 2210 | 1699 | Water | 89.8 | 5 | 516.3 | 10 | 32.5 | 222358 | _ |  | 10 | 910 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 1510 | 247 | X |  |  | AlMg |  | X | X | _
126 | X |  |  | 6870 | 2230 | 2210 | 1965 | Water | 113.8 | 5 | 654.3 | 10 | 39 | 214003 | _ |  | 10 | 910 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 2265 | 370.5 | X |  |  | AlMg |  | X | X | _
127 | X |  |  | 6870 | 2230 | 2210 | 2257 | Water | 127.5 | 5 | 732.9 | 10 | 28.5 | 205736 | _ |  | 10 | 910 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 3020 | 494 | X |  |  | AlMg |  | X | X | _
128 | X |  |  | 8190 | 2230 | 2210 | 1912 | Water | 107.4 | 5 | 617.3 | 10 | 27.8 | 266872 | _ |  | 12 | 910 | 660 | 860 | 19.8 | 3 phase 400V/50Hz | 63 | 1814.3 | 296.8 | X |  |  | AlMg |  | X | X | _
129 | X |  |  | 8190 | 2230 | 2210 | 2230 | Water | 136.6 | 5 | 785.2 | 10 | 38 | 256869 | _ |  | 12 | 910 | 660 | 860 | 19.8 | 3 phase 400V/50Hz | 63 | 2721.6 | 445.2 | X |  |  | AlMg |  | X | X | _
130 | X |  |  | 8190 | 2230 | 2210 | 2655 | Water | 153.5 | 5 | 882.4 | 10 | 31.8 | 246967 | _ |  | 12 | 910 | 660 | 860 | 19.8 | 3 phase 400V/50Hz | 63 | 3628.73 | 593.5 | X |  |  | AlMg |  | X | X | _
131 | X |  |  | 9490 | 2230 | 2210 | 2443 | Water | 126.8 | 5 | 729 | 10 | 43.4 | 311386 | _ |  | 14 | 910 | 660 | 860 | 23.1 | 3 phase 400V/50Hz | 63 | 2118.7 | 346.5 | X |  |  | AlMg |  | X | X | _
132 | X |  |  | 9490 | 2230 | 2210 | 2761 | Water | 158.6 | 5 | 911.9 | 10 | 31.4 | 299735 | _ |  | 14 | 910 | 660 | 860 | 23.1 | 3 phase 400V/50Hz | 63 | 3178 | 519.9 | X |  |  | AlMg |  | X | X | _
133 | X |  |  | 9490 | 2230 | 2210 | 3175 | Water | 180.5 | 5 | 1037.9 | 10 | 49.2 | 288198 | _ |  | 14 | 910 | 660 | 860 | 23.1 | 3 phase 400V/50Hz | 63 | 4237.4 | 693.1 | X |  |  | AlMg |  | X | X | _
134 | X |  |  | 10800 | 2230 | 2210 | 2867 | Water | 146.2 | 5 | 840.9 | 10 | 63.6 | 355900 | _ |  | 16 | 910 | 660 | 860 | 26.4 | 3 phase 400V/50Hz | 64 | 2423 | 396.4 | X |  |  | AlMg |  | X | X | _
135 | X |  |  | 10800 | 2230 | 2210 | 3165 | Water | 183 | 5 | 1052.2 | 10 | 46.4 | 342601 | _ |  | 16 | 910 | 660 | 860 | 26.4 | 3 phase 400V/50Hz | 64 | 3634.5 | 594.6 | X |  |  | AlMg |  | X | X | _
136 | X |  |  | 10800 | 2230 | 2210 | 3590 | Water | 205.1 | 5 | 1179 | 10 | 34.2 | 329429 | _ |  | 16 | 910 | 660 | 860 | 26.4 | 3 phase 400V/50Hz | 64 | 4846 | 792.8 | X |  |  | AlMg |  | X | X | _
137 | X |  |  | 2940 | 2230 | 2210 | 690 | Water | 29.1 | 5 | 167.3 | 10 | 6 | 66534 | _ |  | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 597.5 | 97.6 | X |  |  | AlMg |  | X | X | _
138 | X |  |  | 2940 | 2230 | 2210 | 797 | Water | 34.3 | 5 | 197 | 10 | 4.8 | 59890 | _ |  | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 895.5 | 146.6 | X |  |  | AlMg |  | X | X | _
139 | X |  |  | 2940 | 2230 | 2210 | 913 | Water | 35.8 | 5 | 205.7 | 10 | 3.5 | 53830 | _ |  | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 1194.1 | 195.4 | X |  |  | AlMg |  | X | X | _
140 | X |  |  | 4250 | 2230 | 2210 | 903 | Water | 45.3 | 5 | 260.2 | 10 | 19.2 | 100017 | _ |  | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 901.3 | 147.5 | X |  |  | AlMg |  | X | X | _
141 | X |  |  | 4250 | 2230 | 2210 | 1115 | Water | 53.1 | 5 | 305.2 | 10 | 14.8 | 90155 | _ |  | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 1352.1 | 221.1 | X |  |  | AlMg |  | X | X | _
142 | X |  |  | 4250 | 2230 | 2210 | 1328 | Water | 55.3 | 5 | 317.9 | 10 | 11 | 81107 | _ |  | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 1802.8 | 294.9 | X |  |  | AlMg |  | X | X | _
143 | X |  |  | 5560 | 2230 | 2210 | 1359 | Water | 60.9 | 5 | 349.9 | 10 | 43.2 | 133495 | _ |  | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 1205.7 | 197.1 | X |  |  | AlMg |  | X | X | _
144 | X |  |  | 5560 | 2230 | 2210 | 1572 | Water | 71.1 | 5 | 408.6 | 10 | 33.2 | 120418 | _ |  | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 1808.5 | 295.8 | X |  |  | AlMg |  | X | X | _
145 | X |  |  | 5560 | 2230 | 2210 | 1805 | Water | 74.8 | 5 | 430.1 | 10 | 24.7 | 108381 | _ |  | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 2411.4 | 394.4 | X |  |  | AlMg |  | X | X | _
146 | X |  |  | 6870 | 2230 | 2210 | 1699 | Water | 75.8 | 5 | 436.1 | 10 | 48.1 | 166975 | _ |  | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 1510 | 247 | X |  |  | AlMg |  | X | X | _
147 | X |  |  | 6870 | 2230 | 2210 | 1965 | Water | 89.9 | 5 | 517 | 10 | 30.4 | 150680 | _ |  | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 2265 | 370.5 | X |  |  | AlMg |  | X | X | _
148 | X |  |  | 6870 | 2230 | 2210 | 2257 | Water | 93.4 | 5 | 537.1 | 10 | 45.9 | 135655 | _ |  | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 3020 | 494 | X |  |  | AlMg |  | X | X | _
149 | X |  |  | 8190 | 2230 | 2210 | 1912 | Water | 91.1 | 5 | 524 | 10 | 35.5 | 200453 | _ |  | 12 | 1000 | 250 | 380 | 8.04 | 3 phase 400V/50Hz | 48 | 1814.3 | 296.8 | X |  |  | AlMg |  | X | X | _
150 | X |  |  | 8190 | 2230 | 2210 | 2230 | Water | 107.4 | 5 | 617.8 | 10 | 50.7 | 180941 | _ |  | 12 | 1000 | 250 | 380 | 8.04 | 3 phase 400V/50Hz | 48 | 2721.6 | 445.2 | X |  |  | AlMg |  | X | X | _
151 | X |  |  | 8190 | 2230 | 2210 | 2655 | Water | 111.7 | 5 | 642.3 | 10 | 33.9 | 192929 | _ |  | 12 | 1000 | 250 | 380 | 8.04 | 3 phase 400V/50Hz | 48 | 3628.73 | 593.5 | X |  |  | AlMg |  | X | X | _
152 | X |  |  | 9490 | 2230 | 2210 | 2443 | Water | 105.8 | 5 | 608.4 | 10 | 54.8 | 233931 | _ |  | 14 | 1000 | 250 | 380 | 9.38 | 3 phase 400V/50Hz | 48 | 2118.7 | 346.5 | X |  |  | AlMg |  | X | X | _
153 | X |  |  | 9490 | 2230 | 2210 | 2761 | Water | 125.2 | 5 | 719.9 | 10 | 34.6 | 211202 | _ |  | 14 | 1000 | 250 | 380 | 9.38 | 3 phase 400V/50Hz | 48 | 3178 | 519.9 | X |  |  | AlMg |  | X | X | _
154 | X |  |  | 9490 | 2230 | 2210 | 3175 | Water | 131.2 | 5 | 754.5 | 10 | 52.2 | 190202 | _ |  | 14 | 1000 | 250 | 380 | 9.38 | 3 phase 400V/50Hz | 48 | 4237.4 | 693.1 | X |  |  | AlMg |  | X | X | _
155 | X |  |  | 10800 | 2230 | 2210 | 2867 | Water | 122 | 5 | 701.6 | 10 | 49 | 267410 | _ |  | 16 | 1000 | 250 | 380 | 10.72 | 3 phase 400V/50Hz | 49 | 2423 | 396.4 | X |  |  | AlMg |  | X | X | _
156 | X |  |  | 10800 | 2230 | 2210 | 3165 | Water | 144.1 | 5 | 828.4 | 10 | 50.3 | 241463 | _ |  | 16 | 1000 | 250 | 380 | 10.72 | 3 phase 400V/50Hz | 49 | 3634.5 | 594.6 | X |  |  | AlMg |  | X | X | _
157 | X |  |  | 10800 | 2230 | 2210 | 3590 | Water | 150.8 | 5 | 866.8 | 10 | 33.7 | 217476 | _ |  | 16 | 1000 | 250 | 380 | 10.72 | 3 phase 400V/50Hz | 49 | 4846 | 792.8 | X |  |  | AlMg |  | X | X | _
158 | X |  |  | 1545 | 1214 | 1221 | 115 | Water | 6.2426 | 5 | 36 | 10 | 20.8 | 17747 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 88.2 | 8 | X |  |  |  |  | X |  | 3595 |  |  |  |  | 3595
159 | X |  |  | 1545 | 1214 | 1221 | 125 | Water | 8.3409 | 5 | 48.1 | 10 | 70 | 17182 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 132.3 | 11 | X |  |  |  |  | X |  | 3847 |  |  |  |  | 3847
160 | X |  |  | 1545 | 1214 | 1221 | 135 | Water | 9.5374 | 5 | 55 | 10 | 53.7 | 16576 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 176.5 | 15 | X |  |  |  |  | X |  | 4121 |  |  |  |  | 4121
161 | X |  |  | 1545 | 1214 | 1221 | 145 | Water | 10.283 | 5 | 59.3 | 10 | 40.8 | 15971 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 220.6 | 19 | X |  |  |  |  | X |  | _ |  |  |  |  | _
162 | X |  |  | 2635 | 1214 | 1221 | 230 | Water | 12.8148 | 5 | 73.9 | 10 | 79 | 35414 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 172.6 | 15 | X |  |  |  |  | X |  | 5374 |  |  |  |  | 5374
163 | X |  |  | 2635 | 1214 | 1221 | 250 | Water | 16.439 | 5 | 94.8 | 10 | 59.9 | 34227 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 258.9 | 22 | X |  |  |  |  | X |  | 6024 |  |  |  |  | 6024
164 | X |  |  | 2635 | 1214 | 1221 | 270 | Water | 19.0227 | 5 | 109.7 | 10 | 77.6 | 32966 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 345.2 | 30 | X |  |  |  |  | X |  | 6493 |  |  |  |  | 6493
165 | X |  |  | 2635 | 1214 | 1221 | 290 | Water | 20.4793 | 5 | 118.1 | 10 | 59.3 | 31714 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 431.5 | 37 | X |  |  |  |  | X |  | _ |  |  |  |  | _
166 | X |  |  | 4655 | 1214 | 1221 | 345 | Water | 18.9707 | 5 | 109.4 | 10 | 54.9 | 53078 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 256.9 | 22 | X |  |  |  |  | X |  | 7075 |  |  |  |  | 7075
167 | X |  |  | 4655 | 1214 | 1221 | 375 | Water | 24.3637 | 5 | 140.5 | 10 | 41.7 | 51269 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 385.4 | 33 | X |  |  |  |  | X |  | 7948 |  |  |  |  | 7948
168 | X |  |  | 4655 | 1214 | 1221 | 405 | Water | 28.404 | 5 | 163.8 | 10 | 73.3 | 49351 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 513.9 | 44 | X |  |  |  |  | X |  | 8575 |  |  |  |  | 8575
169 | X |  |  | 4655 | 1214 | 1221 | 435 | Water | 30.589 | 5 | 176.4 | 10 | 58.3 | 47454 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 642.4 | 55 | X |  |  |  |  | X |  | _ |  |  |  |  | _
170 | X |  |  | 4815 | 1214 | 1221 | 460 | Water | 25.0053 | 5 | 144.2 | 10 | 37.8 | 70742 | _ | 1 | 4 | 630 | 1000 | 1310 | 10.4 | 3 phase 400V/50Hz | 62 | 341.3 | 29 | X |  |  |  |  | X |  | 9498 |  |  |  |  | 9498
171 | X |  |  | 4815 | 1214 | 1221 | 500 | Water | 32.1323 | 5 | 185.3 | 10 | 28.7 | 68310 | _ | 1 | 4 | 630 | 1000 | 1310 | 10.4 | 3 phase 400V/50Hz | 62 | 512 | 44 | X |  |  |  |  | X |  | 10196 |  |  |  |  | 10196
172 | X |  |  | 4815 | 1214 | 1221 | 540 | Water | 36.8489 | 5 | 212.5 | 10 | 22.1 | 65736 | _ | 1 | 4 | 630 | 1000 | 1310 | 10.4 | 3 phase 400V/50Hz | 62 | 682.6 | 59 | X |  |  |  |  | X |  | 10979 |  |  |  |  | 10979
173 | X |  |  | 4815 | 1214 | 1221 | 580 | Water | 40.6466 | 5 | 234.4 | 10 | 54.1 | 63192 | _ | 1 | 4 | 630 | 1000 | 1310 | 10.4 | 3 phase 400V/50Hz | 62 | 853.3 | 74 | X |  |  |  |  | X |  | _ |  |  |  |  | _
174 | X |  |  | 1855 | 1214 | 1221 | 145 | Water | 7.1964 | 5 | 41.5 | 10 | 32.6 | 18073 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 88.2 | 8 | X |  |  |  |  | X |  | 3860 |  |  |  |  | 3860
175 | X |  |  | 1855 | 1214 | 1221 | 160 | Water | 9.1559 | 5 | 52.8 | 10 | 24.3 | 17748 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 132.3 | 11 | X |  |  |  |  | X |  | 4169 |  |  |  |  | 4169
176 | X |  |  | 1855 | 1214 | 1221 | 175 | Water | 10.6472 | 5 | 61.4 | 10 | 42.5 | 17379 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 176.5 | 15 | X |  |  |  |  | X |  | 4474 |  |  |  |  | 4474
177 | X |  |  | 1855 | 1214 | 1221 | 190 | Water | 11.4795 | 5 | 66.2 | 10 | 36.7 | 16984 | _ | 1 | 1 | 630 | 1000 | 1310 | 2.6 | 3 phase 400V/50Hz | 56 | 220.6 | 19 | X |  |  |  |  | X |  | _ |  |  |  |  | _
178 | X |  |  | 3255 | 1214 | 1221 | 290 | Water | 14.5488 | 5 | 83.9 | 10 | 66.3 | 36111 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 172.6 | 15 | X |  |  |  |  | X |  | 5920 |  |  |  |  | 5920
179 | X |  |  | 3255 | 1214 | 1221 | 320 | Water | 18.5198 | 5 | 106.8 | 10 | 52.8 | 35434 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 258.9 | 22 | X |  |  |  |  | X |  | 6721 |  |  |  |  | 6721
180 | X |  |  | 3255 | 1214 | 1221 | 350 | Water | 21.329 | 5 | 123 | 10 | 71.3 | 34666 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 345.2 | 30 | X |  |  |  |  | X |  | 7262 |  |  |  |  | 7262
181 | X |  |  | 3255 | 1214 | 1221 | 380 | Water | 22.9591 | 5 | 132.4 | 10 | 54.6 | 33848 | _ | 1 | 2 | 630 | 1000 | 1310 | 5.2 | 3 phase 400V/50Hz | 59 | 431.5 | 37 | X |  |  |  |  | X |  | _ |  |  |  |  | _
182 | X |  |  | 4655 | 1214 | 1221 | 435 | Water | 21.8839 | 5 | 126.2 | 10 | 89.1 | 54148 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 256.9 | 22 | X |  |  |  |  | X |  | 7701 |  |  |  |  | 7701
183 | X |  |  | 4655 | 1214 | 1221 | 480 | Water | 27.8665 | 5 | 160.7 | 10 | 67 | 53118 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 385.4 | 33 | X |  |  |  |  | X |  | 8360 |  |  |  |  | 8360
184 | X |  |  | 4655 | 1214 | 1221 | 525 | Water | 31.7334 | 5 | 183 | 10 | 50.5 | 51951 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 513.9 | 44 | X |  |  |  |  | X |  | 9086 |  |  |  |  | 9086
185 | X |  |  | 4655 | 1214 | 1221 | 570 | Water | 34.1785 | 5 | 197.1 | 10 | 38.7 | 50709 | _ | 1 | 3 | 630 | 1000 | 1310 | 7.8 | 3 phase 400V/50Hz | 61 | 642.4 | 55 | X |  |  |  |  | X |  | _ |  |  |  |  | _
186 | X |  |  | 2205 | 1454 | 1252 | 180 | Water | 9.7975 | 5 | 56.5 | 10 | 49 | 22304 | _ | 1 | 1 | 800 | 660 | 880 | 2 | 3 phase 400V/50Hz | 51 | 167.2 | 14 | X |  |  |  |  | X |  | 4770 |  |  |  |  | 4770
187 | X |  |  | 2205 | 1454 | 1252 | 200 | Water | 12.1732 | 5 | 70.2 | 10 | 35.3 | 21676 | _ | 1 | 1 | 800 | 660 | 880 | 2 | 3 phase 400V/50Hz | 51 | 250.8 | 22 | X |  |  |  |  | X |  | 5143 |  |  |  |  | 5143
188 | X |  |  | 2205 | 1454 | 1252 | 220 | Water | 13.7858 | 5 | 79.5 | 10 | 58.3 | 21055 | _ | 1 | 1 | 800 | 660 | 880 | 2 | 3 phase 400V/50Hz | 51 | 334.3 | 29 | X |  |  |  |  | X |  | 5590 |  |  |  |  | 5590
189 | X |  |  | 2205 | 1454 | 1252 | 240 | Water | 14.6182 | 5 | 84.3 | 10 | 46.5 | 20452 | _ | 1 | 1 | 800 | 660 | 880 | 2 | 3 phase 400V/50Hz | 51 | 417.9 | 36 | X |  |  |  |  | X |  | _ |  |  |  |  | _
190 | X |  |  | 3955 | 1454 | 1252 | 360 | Water | 19.4216 | 5 | 112 | 10 | 44.1 | 44548 | _ | 1 | 2 | 800 | 660 | 880 | 4 | 3 phase 400V/50Hz | 54 | 329.7 | 28 | X |  |  |  |  | X |  | 7542 |  |  |  |  | 7542
191 | X |  |  | 3955 | 1454 | 1252 | 400 | Water | 24.5371 | 5 | 141.5 | 10 | 72.7 | 43262 | _ | 1 | 2 | 800 | 660 | 880 | 4 | 3 phase 400V/50Hz | 54 | 494.5 | 43 | X |  |  |  |  | X |  | 8169 |  |  |  |  | 8169
192 | X |  |  | 3955 | 1454 | 1252 | 440 | Water | 27.3983 | 5 | 158 | 10 | 52.7 | 41993 | _ | 1 | 2 | 800 | 660 | 880 | 4 | 3 phase 400V/50Hz | 54 | 659.4 | 57 | X |  |  |  |  | X |  | 9316 |  |  |  |  | 9316
193 | X |  |  | 3955 | 1454 | 1252 | 480 | Water | 29.2364 | 5 | 168.6 | 10 | 74.3 | 40762 | _ | 1 | 2 | 800 | 660 | 880 | 4 | 3 phase 400V/50Hz | 54 | 824.2 | 71 | X |  |  |  |  | X |  | _ |  |  |  |  | _
194 | X |  |  | 5705 | 1454 | 1252 | 540 | Water | 29.0456 | 5 | 167.5 | 10 | 42.5 | 66791 | _ | 1 | 3 | 800 | 660 | 880 | 6 | 3 phase 400V/50Hz | 56 | 492.2 | 42 | X |  |  |  |  | X |  | 10754 |  |  |  |  | 10754
195 | X |  |  | 5705 | 1454 | 1252 | 600 | Water | 36.1553 | 5 | 208.5 | 10 | 30.7 | 64848 | _ | 1 | 3 | 800 | 660 | 880 | 6 | 3 phase 400V/50Hz | 56 | 738.3 | 64 | X |  |  |  |  | X |  | 11752 |  |  |  |  | 11752
196 | X |  |  | 5705 | 1454 | 1252 | 660 | Water | 41.1841 | 5 | 237.5 | 10 | 71.1 | 62929 | _ | 1 | 3 | 800 | 660 | 880 | 6 | 3 phase 400V/50Hz | 56 | 984.5 | 85 | X |  |  |  |  | X |  | 12529 |  |  |  |  | 12529
197 | X |  |  | 5705 | 1454 | 1252 | 720 | Water | 43.5945 | 5 | 251.4 | 10 | 53.2 | 61071 | _ | 1 | 3 | 800 | 660 | 880 | 6 | 3 phase 400V/50Hz | 56 | 1230.6 | 106 | X |  |  |  |  | X |  | _ |  |  |  |  | _
198 | X |  |  | 7455 | 1454 | 1252 | 720 | Water | 39.3287 | 5 | 226.8 | 10 | 95.7 | 89034 | _ | 1 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 57 | 654.8 | 57 | X |  |  |  |  | X |  | 14118 |  |  |  |  | 14118
199 | X |  |  | 7455 | 1454 | 1252 | 800 | Water | 48.9007 | 5 | 282 | 10 | 68.9 | 86432 | _ | 1 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 57 | 982.1 | 85 | X |  |  |  |  | X |  | 15685 |  |  |  |  | 15685
200 | X |  |  | 7455 | 1454 | 1252 | 880 | Water | 54.5885 | 5 | 314.8 | 10 | 50 | 83865 | _ | 1 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 57 | 1309.5 | 113 | X |  |  |  |  | X |  | 17482 |  |  |  |  | 17482
201 | X |  |  | 7455 | 1454 | 1252 | 960 | Water | 57.8138 | 5 | 333.4 | 10 | 37.4 | 81380 | _ | 1 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 57 | 1636.9 | 141 | X |  |  |  |  | X |  | _ |  |  |  |  | _
202 | X |  |  | 9205 | 1454 | 1252 | 900 | Water | 47.6522 | 5 | 274.8 | 10 | 24.2 | 111277 | _ | 1 | 5 | 800 | 660 | 880 | 10 | 3 phase 400V/50Hz | 58 | 817.3 | 71 | X |  |  |  |  | X |  | 17138 |  |  |  |  | 17138
203 | X |  |  | 9205 | 1454 | 1252 | 1000 | Water | 59.3745 | 5 | 342.4 | 10 | 17.5 | 108017 | _ | 1 | 5 | 800 | 660 | 880 | 10 | 3 phase 400V/50Hz | 58 | 1225.9 | 106 | X |  |  |  |  | X |  | 18839 |  |  |  |  | 18839
204 | X |  |  | 9205 | 1454 | 1252 | 1100 | Water | 68.7731 | 5 | 396.6 | 10 | 93.2 | 104800 | _ | 1 | 5 | 800 | 660 | 880 | 10 | 3 phase 400V/50Hz | 58 | 1634.6 | 141 | X |  |  |  |  | X |  | 21202 |  |  |  |  | 21202
205 | X |  |  | 9205 | 1454 | 1252 | 1200 | Water | 72.7962 | 5 | 419.8 | 10 | 69.7 | 101688 | _ | 1 | 5 | 800 | 660 | 880 | 10 | 3 phase 400V/50Hz | 58 | 2043.2 | 176 | X |  |  |  |  | X |  | _ |  |  |  |  | _
206 | X |  |  | 2555 | 1454 | 1289 | 215 | Water | 10.8032 | 5 | 62.3 | 10 | 68 | 22865 | _ | 1 | 1 | 900 | 660 | 860 | 1.65 | 3 phase 400V/50Hz | 53 | 199.7 | 17 | X |  |  |  |  | X |  | 5021 |  |  |  |  | 5021
207 | X |  |  | 2555 | 1454 | 1289 | 240 | Water | 13.3003 | 5 | 76.7 | 10 | 48.1 | 22382 | _ | 1 | 1 | 900 | 660 | 860 | 1.65 | 3 phase 400V/50Hz | 53 | 299.5 | 26 | X |  |  |  |  | X |  | 5438 |  |  |  |  | 5438
208 | X |  |  | 2555 | 1454 | 1289 | 265 | Water | 14.9303 | 5 | 86.1 | 10 | 78.6 | 21878 | _ | 1 | 1 | 900 | 660 | 860 | 1.65 | 3 phase 400V/50Hz | 53 | 399.4 | 34 | X |  |  |  |  | X |  | 6219 |  |  |  |  | 6219
209 | X |  |  | 2555 | 1454 | 1289 | 290 | Water | 22.0747 | 5 | 127.3 | 10 | 47.2 | 33402 | _ | 1 | 1 | 900 | 660 | 860 | 1.65 | 3 phase 400V/50Hz | 53 | 499.2 | 43 | X |  |  |  |  | X |  | _ |  |  |  |  | _
210 | X |  |  | 4655 | 1454 | 1289 | 430 | Water | 21.4504 | 5 | 123.7 | 10 | 62.3 | 45693 | _ | 1 | 2 | 900 | 660 | 860 | 3.3 | 3 phase 400V/50Hz | 56 | 394.7 | 34 | X |  |  |  |  | X |  | 8011 |  |  |  |  | 8011
211 | X |  |  | 4655 | 1454 | 1289 | 480 | Water | 26.4445 | 5 | 152.5 | 10 | 44.1 | 44704 | _ | 1 | 2 | 900 | 660 | 860 | 3.3 | 3 phase 400V/50Hz | 56 | 592.1 | 51 | X |  |  |  |  | X |  | 9161 |  |  |  |  | 9161
212 | X |  |  | 4655 | 1454 | 1289 | 530 | Water | 29.7219 | 5 | 171.4 | 10 | 72.3 | 43676 | _ | 1 | 2 | 900 | 660 | 860 | 3.3 | 3 phase 400V/50Hz | 56 | 789.4 | 68 | X |  |  |  |  | X |  | 10068 |  |  |  |  | 10068
213 | X |  |  | 4655 | 1454 | 1289 | 580 | Water | 31.3346 | 5 | 180.7 | 10 | 53.5 | 42637 | _ | 1 | 2 | 900 | 660 | 860 | 3.3 | 3 phase 400V/50Hz | 56 | 986.8 | 85 | X |  |  |  |  | X |  | _ |  |  |  |  | _
214 | X |  |  | 6755 | 1454 | 1289 | 645 | Water | 32.1149 | 5 | 185.2 | 10 | 60.5 | 68521 | _ | 1 | 3 | 900 | 660 | 860 | 4.95 | 3 phase 400V/50Hz | 58 | 589.7 | 51 | X |  |  |  |  | X |  | 11835 |  |  |  |  | 11835
215 | X |  |  | 6755 | 1454 | 1289 | 720 | Water | 39.5888 | 5 | 228.3 | 10 | 42.8 | 67026 | _ | 1 | 3 | 900 | 660 | 860 | 4.95 | 3 phase 400V/50Hz | 58 | 884.6 | 76 | X |  |  |  |  | X |  | 13186 |  |  |  |  | 13186
216 | X |  |  | 6755 | 1454 | 1289 | 795 | Water | 44.6696 | 5 | 257.6 | 10 | 98 | 65472 | _ | 1 | 3 | 900 | 660 | 860 | 4.95 | 3 phase 400V/50Hz | 58 | 1179.5 | 102 | X |  |  |  |  | X |  | 14020 |  |  |  |  | 14020
217 | X |  |  | 6755 | 1454 | 1289 | 870 | Water | 47.0799 | 5 | 271.5 | 10 | 72.5 | 63904 | _ | 1 | 3 | 900 | 660 | 860 | 4.95 | 3 phase 400V/50Hz | 58 | 1474.4 | 127 | X |  |  |  |  | X |  | _ |  |  |  |  | _
218 | X |  |  | 8855 | 1454 | 1289 | 860 | Water | 41.6003 | 5 | 239.9 | 10 | 18.3 | 91348 | _ | 1 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 59 | 784.8 | 68 | X |  |  |  |  | X |  | 15297 |  |  |  |  | 15297
219 | X |  |  | 8855 | 1454 | 1289 | 960 | Water | 53.4093 | 5 | 308 | 10 | 95.9 | 89347 | _ | 1 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 59 | 1177.2 | 102 | X |  |  |  |  | X |  | 16847 |  |  |  |  | 16847
220 | X |  |  | 8855 | 1454 | 1289 | 1060 | Water | 59.2704 | 5 | 341.8 | 10 | 69.2 | 87268 | _ | 1 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 59 | 1569.6 | 135 | X |  |  |  |  | X |  | 18949 |  |  |  |  | 18949
221 | X |  |  | 8855 | 1454 | 1289 | 1160 | Water | 62.5131 | 5 | 360.5 | 10 | 51.2 | 85171 | _ | 1 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 59 | 1961.9 | 169 | X |  |  |  |  | X |  | _ |  |  |  |  | _
222 | X |  |  | 2555 | 1454 | 1295 | 215 | Water | 9.3102 | 5 | 53.69 | 10 | 52.33 | 18021 | _ | 1 | 1 | 1000 | 250 | 380 | 0.67 | 3 phase 400V/50Hz | 38 | 199.7 | 17 | X |  |  |  |  | X |  | 5179 |  |  |  |  | 5179
223 | X |  |  | 2555 | 1454 | 1295 | 240 | Water | 10.9056 | 5 | 62.89 | 10 | 33.69 | 16984 | _ | 1 | 1 | 1000 | 250 | 380 | 0.67 | 3 phase 400V/50Hz | 38 | 299.5 | 26 | X |  |  |  |  | X |  | 5597 |  |  |  |  | 5597
224 | X |  |  | 4655 | 1454 | 1295 | 430 | Water | 18.4886 | 5 | 106.62 | 10 | 47.91 | 35951 | _ | 1 | 2 | 1000 | 250 | 380 | 1.34 | 3 phase 400V/50Hz | 41 | 394.7 | 34 | X |  |  |  |  | X |  | 8322 |  |  |  |  | 8322
225 | X |  |  | 4655 | 1454 | 1295 | 480 | Water | 21.929 | 5 | 126.46 | 10 | 70.22 | 33851 | _ | 1 | 2 | 1000 | 250 | 380 | 1.34 | 3 phase 400V/50Hz | 41 | 592.1 | 51 | X |  |  |  |  | X |  | 9472 |  |  |  |  | 9472
226 | X |  |  | 6755 | 1454 | 1295 | 645 | Water | 27.6636 | 5 | 159.53 | 10 | 46.45 | 53881 | _ | 1 | 3 | 1000 | 250 | 380 | 2.01 | 3 phase 400V/50Hz | 43 | 589.7 | 51 | X |  |  |  |  | X |  | 12328 |  |  |  |  | 12328
227 | X |  |  | 6755 | 1454 | 1295 | 720 | Water | 32.9542 | 5 | 190.04 | 10 | 95.09 | 50716 | _ | 1 | 3 | 1000 | 250 | 380 | 2.01 | 3 phase 400V/50Hz | 43 | 884.6 | 76 | X |  |  |  |  | X |  | 13666 |  |  |  |  | 13666
228 | X |  |  | 8855 | 1454 | 1295 | 860 | Water | 37.3761 | 5 | 215.54 | 10 | 105.03 | 71810 | _ | 1 | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 44 | 784.8 | 68 | X |  |  |  |  | X |  | 15920 |  |  |  |  | 15920
229 | X |  |  | 8855 | 1454 | 1295 | 960 | Water | 43.7124 | 5 | 252.08 | 10 | 67.1 | 67581 | _ | 1 | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 44 | 1177.2 | 102 | X |  |  |  |  | X |  | 17471 |  |  |  |  | 17471
230 | X |  |  | 3955 | 2249 | 1252 | 580 | Water | 34.1265 | 5 | 196.8 | 10 | 52 | 86375 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 512.9 | 44 | X |  |  |  |  | X |  | 11747 |  |  |  |  | 11747
231 | X |  |  | 3955 | 2249 | 1252 | 600 | Water | 43.5945 | 5 | 251.4 | 10 | 92 | 82528 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 769.3 | 66 | X |  |  |  |  | X |  | 13047 |  |  |  |  | 13047
232 | X |  |  | 3955 | 2249 | 1252 | 646 | Water | 48.8834 | 5 | 281.9 | 10 | 68 | 78902 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 1025.7 | 87 | X |  |  |  |  | X |  | 14347 |  |  |  |  | 14347
233 | X |  |  | 3955 | 2249 | 1252 | 711 | Water | 52.1608 | 5 | 300.8 | 10 | 95 | 75556 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 1282.2 | 109 | X |  |  |  |  | X |  | _ |  |  |  |  | _
234 | X |  |  | 5705 | 2249 | 1252 | 713 | Water | 51.0856 | 5 | 294.6 | 10 | 53 | 129469 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 765.7 | 66 | X |  |  |  |  | X |  | 15850 |  |  |  |  | 15850
235 | X |  |  | 5705 | 2249 | 1252 | 820 | Water | 64.0911 | 5 | 369.6 | 10 | 38 | 123657 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1148.5 | 99 | X |  |  |  |  | X |  | 18850 |  |  |  |  | 18850
236 | X |  |  | 5705 | 2249 | 1252 | 920 | Water | 73.4898 | 5 | 423.8 | 10 | 94 | 118187 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1531.4 | 132 | X |  |  |  |  | X |  | 20350 |  |  |  |  | 20350
237 | X |  |  | 5705 | 2249 | 1252 | 1012 | Water | 77.7209 | 5 | 448.2 | 10 | 66 | 113142 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1914.2 | 165 | X |  |  |  |  | X |  | _ |  |  |  |  | _
238 | X |  |  | 7455 | 2249 | 1252 | 1020 | Water | 69.2066 | 5 | 399.1 | 10 | 119 | 172562 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1018.5 | 88 | X |  |  |  |  | X |  | 21240 |  |  |  |  | 21240
239 | X |  |  | 7455 | 2249 | 1252 | 1062 | Water | 86.7901 | 5 | 500.5 | 10 | 87 | 164785 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1527.8 | 132 | X |  |  |  |  | X |  | 23790 |  |  |  |  | 23790
240 | X |  |  | 7455 | 2249 | 1252 | 1196 | Water | 97.3332 | 5 | 561.3 | 10 | 64 | 157470 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 2037 | 176 | X |  |  |  |  | X |  | 26340 |  |  |  |  | 26340
241 | X |  |  | 7455 | 2249 | 1252 | 1316 | Water | 103.021 | 5 | 594.1 | 10 | 48 | 150728 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 2546.3 | 220 | X |  |  |  |  | X |  | _ |  |  |  |  | _
242 | X |  |  | 9205 | 2249 | 1252 | 1330 | Water | 83.7555 | 5 | 483 | 10 | 30.1 | 215655 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 1271.3 | 110 | X |  |  |  |  | X |  | 25702 |  |  |  |  | 25702
243 | X |  |  | 9205 | 2249 | 1252 | 1175 | Water | 105.1539 | 5 | 606.4 | 10 | 22 | 205913 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 1907 | 164 | X |  |  |  |  | X |  | 29352 |  |  |  |  | 29352
244 | X |  |  | 9205 | 2249 | 1252 | 1473 | Water | 122.668 | 5 | 707.4 | 10 | 120 | 196753 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 2542.7 | 219 | X |  |  |  |  | X |  | 32952 |  |  |  |  | 32952
245 | X |  |  | 9205 | 2249 | 1252 | 1620 | Water | 129.7603 | 5 | 748.3 | 10 | 89 | 188313 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 3178.3 | 274 | X |  |  |  |  | X |  | _ |  |  |  |  | _
246 | X |  |  | 10955 | 2249 | 1252 | 1640 | Water | 101.8245 | 5 | 587.2 | 10 | 50.9 | 258748 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 1524.2 | 132 | X |  |  |  |  | X |  | 29619 |  |  |  |  | 29619
247 | X |  |  | 10955 | 2249 | 1252 | 1396 | Water | 127.7488 | 5 | 736.7 | 10 | 37 | 247041 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 2286.2 | 197 | X |  |  |  |  | X |  | 34369 |  |  |  |  | 34369
248 | X |  |  | 10955 | 2249 | 1252 | 1745 | Water | 143.4768 | 5 | 827.4 | 10 | 27 | 236036 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 3048.3 | 263 | X |  |  |  |  | X |  | 39119 |  |  |  |  | 39119
249 | X |  |  | 10955 | 2249 | 1252 | 1920 | Water | 152.1645 | 5 | 877.5 | 10 | 20 | 225898 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 3810.4 | 328 | X |  |  |  |  | X |  | _ |  |  |  |  | _
250 | X |  |  | 4655 | 2249 | 1289 | 951 | Water | 37.0744 | 5 | 213.8 | 10 | 24.3 | 89290 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 614 | 52.9 | X |  |  |  |  | X |  | 12185 |  |  |  |  | 12185
251 | X |  |  | 4655 | 2249 | 1289 | 870 | Water | 47.5135 | 5 | 274 | 10 | 57 | 86131 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 921 | 79.4 | X |  |  |  |  | X |  | 14185 |  |  |  |  | 14185
252 | X |  |  | 4655 | 2249 | 1289 | 930 | Water | 53.0625 | 5 | 306 | 10 | 42.7 | 82981 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 1228 | 105.8 | X |  |  |  |  | X |  | 16185 |  |  |  |  | 16185
253 | X |  |  | 4655 | 2249 | 1289 | 1000 | Water | 56.6347 | 5 | 326.6 | 10 | 69.8 | 79949 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 1535 | 132.3 | X |  |  |  |  | X |  | _ |  |  |  |  | _
254 | X |  |  | 6755 | 2249 | 1289 | 1050 | Water | 57.0508 | 5 | 329 | 10 | 76.5 | 133872 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 917.4 | 79.1 | X |  |  |  |  | X |  | 16384 |  |  |  |  | 16384
255 | X |  |  | 6755 | 2249 | 1289 | 1070 | Water | 71.0968 | 5 | 410 | 10 | 55.3 | 129101 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1376.1 | 118.6 | X |  |  |  |  | X |  | 19334 |  |  |  |  | 19334
256 | X |  |  | 6755 | 2249 | 1289 | 1163 | Water | 79.403 | 5 | 457.9 | 10 | 40.5 | 124348 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1834.8 | 158.1 | X |  |  |  |  | X |  | 22334 |  |  |  |  | 22334
257 | X |  |  | 6755 | 2249 | 1289 | 1249 | Water | 85.0907 | 5 | 490.7 | 10 | 92.6 | 119776 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 2293.5 | 197.6 | X |  |  |  |  | X |  | _ |  |  |  |  | _
258 | X |  |  | 8855 | 2249 | 1289 | 1300 | Water | 73.854 | 5 | 425.9 | 10 | 23.1 | 178455 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1220.8 | 105.2 | X |  |  |  |  | X |  | 19175 |  |  |  |  | 19175
259 | X |  |  | 8855 | 2249 | 1289 | 1438 | Water | 92.1484 | 5 | 531.4 | 10 | 16.7 | 172071 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1831.1 | 157.8 | X |  |  |  |  | X |  | 24625 |  |  |  |  | 24625
260 | X |  |  | 8855 | 2249 | 1289 | 1530 | Water | 106.992 | 5 | 617 | 10 | 89.8 | 165714 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 2441.5 | 210.3 | X |  |  |  |  | X |  | 30125 |  |  |  |  | 30125
261 | X |  |  | 8855 | 2249 | 1289 | 1643 | Water | 112.9225 | 5 | 651.2 | 10 | 66.7 | 159603 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 3051.9 | 262.9 | X |  |  |  |  | X |  | _ |  |  |  |  | _
262 | X |  |  | 10955 | 2249 | 1289 | 1625 | Water | 93.8131 | 5 | 541 | 10 | 44 | 223037 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 1524.2 | 131.3 | X |  |  |  |  | X |  | 26636 |  |  |  |  | 26636
263 | X |  |  | 10955 | 2249 | 1289 | 1890 | Water | 117.0149 | 5 | 674.8 | 10 | 31.9 | 215040 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 2286.2 | 197 | X |  |  |  |  | X |  | 32086 |  |  |  |  | 32086
264 | X |  |  | 10955 | 2249 | 1289 | 2080 | Water | 130.7661 | 5 | 754.1 | 10 | 23.3 | 207080 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 3048.3 | 262.6 | X |  |  |  |  | X |  | 37586 |  |  |  |  | 37586
265 | X |  |  | 10955 | 2249 | 1289 | 2234 | Water | 138.2572 | 5 | 797.3 | 10 | 17.2 | 199429 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 3810.4 | 328.2 | X |  |  |  |  | X |  | _ |  |  |  |  | _
266 | X |  |  | 4655 | 2249 | 1278 | 951 | Water | 32.3057 | 5 | 186.3 | 10 | 56.01 | 67468 | _ | 2 | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 614 | 52.9 | X |  |  |  |  | X |  | 12794 |  |  |  |  | 12794
267 | X |  |  | 4655 | 2249 | 1278 | 870 | Water | 38.1322 | 5 | 219.9 | 10 | 86.23 | 61296 | _ | 2 | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 921 | 79.4 | X |  |  |  |  | X |  | 14794 |  |  |  |  | 14794
268 | X |  |  | 6755 | 2249 | 1278 | 1050 | Water | 48.3805 | 5 | 279 | 10 | 57.12 | 101081 | _ | 2 | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 917.4 | 79.1 | X |  |  |  |  | X |  | 17297 |  |  |  |  | 17297
269 | X |  |  | 6755 | 2249 | 1278 | 1070 | Water | 56.3052 | 5 | 324.7 | 10 | 36.51 | 91759 | _ | 2 | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 1376.1 | 118.6 | X |  |  |  |  | X |  | 20247 |  |  |  |  | 20247
270 | X |  |  | 8855 | 2249 | 1278 | 1300 | Water | 62.6692 | 5 | 361.4 | 10 | 17.31 | 134692 | _ | 2 | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 1220.8 | 105.2 | X |  |  |  |  | X |  | 20393 |  |  |  |  | 20393
271 | X |  |  | 8855 | 2249 | 1278 | 1438 | Water | 75.9348 | 5 | 437.9 | 10 | 82.25 | 122221 | _ | 2 | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 1831.1 | 157.8 | X |  |  |  |  | X |  | 25843 |  |  |  |  | 25843
272 | X |  |  | 10955 | 2249 | 1278 | 1625 | Water | 79.559 | 5 | 458.8 | 10 | 32.86 | 168304 | _ | 2 | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 1524.2 | 131.3 | X |  |  |  |  | X |  | 28159 |  |  |  |  | 28159
273 | X |  |  | 10955 | 2249 | 1278 | 1890 | Water | 92.6686 | 5 | 534.4 | 10 | 21.05 | 152683 | _ | 2 | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 2286.2 | 197 | X |  |  |  |  | X |  | 33609 |  |  |  |  | 33609
274 | X |  |  | 3955 | 2249 | 1252 | 602 | Water | 32.1496 | 5 | 185.4 | 10 | 54.3 | 85251 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 479.6 | 77 | X |  |  |  |  | X |  | _ |  |  |  |  | _
275 | X |  |  | 3955 | 2249 | 1252 | 623 | Water | 40.8026 | 5 | 235.3 | 10 | 63.6 | 80929 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 719.3 | 116 | X |  |  |  |  | X |  | _ |  |  |  |  | _
276 | X |  |  | 3955 | 2249 | 1252 | 670 | Water | 45.7967 | 5 | 264.1 | 10 | 44.7 | 76940 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 959 | 153 | X |  |  |  |  | X |  | _ |  |  |  |  | _
277 | X |  |  | 3955 | 2249 | 1252 | 738 | Water | 48.6059 | 5 | 280.3 | 10 | 36.3 | 73324 | _ | 2 | 4 | 800 | 660 | 880 | 8 | 3 phase 400V/50Hz | 56 | 1198.9 | 192 | X |  |  |  |  | X |  | _ |  |  |  |  | _
278 | X |  |  | 5705 | 2249 | 1252 | 740 | Water | 47.5308 | 5 | 274.1 | 10 | 34.7 | 127770 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 715.9 | 116 | X |  |  |  |  | X |  | _ |  |  |  |  | _
279 | X |  |  | 5705 | 2249 | 1252 | 851 | Water | 61.0045 | 5 | 351.8 | 10 | 61.3 | 121245 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1073.8 | 174 | X |  |  |  |  | X |  | _ |  |  |  |  | _
280 | X |  |  | 5705 | 2249 | 1252 | 955 | Water | 68.5477 | 5 | 395.3 | 10 | 45.4 | 115228 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1431.9 | 232 | X |  |  |  |  | X |  | _ |  |  |  |  | _
281 | X |  |  | 5705 | 2249 | 1252 | 1050 | Water | 72.6401 | 5 | 418.9 | 10 | 33.6 | 109781 | _ | 2 | 6 | 800 | 660 | 880 | 12 | 3 phase 400V/50Hz | 58 | 1789.8 | 291 | X |  |  |  |  | X |  | _ |  |  |  |  | _
282 | X |  |  | 7455 | 2249 | 1252 | 1058 | Water | 64.6114 | 5 | 372.6 | 10 | 78.4 | 170288 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 952.3 | 155 | X |  |  |  |  | X |  | _ |  |  |  |  | _
283 | X |  |  | 7455 | 2249 | 1252 | 1102 | Water | 81.2237 | 5 | 468.4 | 10 | 60.2 | 161559 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1428.5 | 232 | X |  |  |  |  | X |  | _ |  |  |  |  | _
284 | X |  |  | 7455 | 2249 | 1252 | 1241 | Water | 91.2813 | 5 | 526.4 | 10 | 45.7 | 153515 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 1904.6 | 310 | X |  |  |  |  | X |  | _ |  |  |  |  | _
285 | X |  |  | 7455 | 2249 | 1252 | 1365 | Water | 98.0269 | 5 | 565.3 | 10 | 75.4 | 146237 | _ | 2 | 8 | 800 | 660 | 880 | 16 | 3 phase 400V/50Hz | 59 | 2380.8 | 387 | X |  |  |  |  | X |  | _ |  |  |  |  | _
286 | X |  |  | 9205 | 2249 | 1252 | 1219 | Water | 100.2118 | 5 | 577.9 | 10 | 35.1 | 201873 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 1783 | 289 | X |  |  |  |  | X |  | _ |  |  |  |  | _
287 | X |  |  | 9205 | 2249 | 1252 | 1528 | Water | 115.2808 | 5 | 664.8 | 10 | 85.5 | 191801 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 2377.4 | 386 | X |  |  |  |  | X |  | _ |  |  |  |  | _
288 | X |  |  | 9205 | 2249 | 1252 | 1681 | Water | 122.061 | 5 | 703.9 | 10 | 60.8 | 182693 | _ | 2 | 10 | 800 | 660 | 880 | 20 | 3 phase 400V/50Hz | 60 | 2971.7 | 483 | X |  |  |  |  | X |  | _ |  |  |  |  | _
289 | X |  |  | 10955 | 2249 | 1252 | 1448 | Water | 121.6275 | 5 | 701.4 | 10 | 59 | 242186 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 2137.6 | 347 | X |  |  |  |  | X |  | _ |  |  |  |  | _
290 | X |  |  | 10955 | 2249 | 1252 | 1810 | Water | 136.6445 | 5 | 788 | 10 | 43.7 | 230088 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 2850.2 | 463 | X |  |  |  |  | X |  | _ |  |  |  |  | _
291 | X |  |  | 10955 | 2249 | 1252 | 1992 | Water | 144.812 | 5 | 835.1 | 10 | 32.3 | 219149 | _ | 2 | 12 | 800 | 660 | 880 | 24 | 3 phase 400V/50Hz | 61 | 3562.7 | 578 | X |  |  |  |  | X |  | _ |  |  |  |  | _
292 | X |  |  | 4655 | 2249 | 1289 | 987 | Water | 35.1322 | 5 | 202.6 | 10 | 38.5 | 88388 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 574.1 | 93 | X |  |  |  |  | X |  | _ |  |  |  |  | _
293 | X |  |  | 4655 | 2249 | 1289 | 903 | Water | 44.6349 | 5 | 257.4 | 10 | 51.8 | 84761 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 861.1 | 140 | X |  |  |  |  | X |  | _ |  |  |  |  | _
294 | X |  |  | 4655 | 2249 | 1289 | 965 | Water | 50.0452 | 5 | 288.6 | 10 | 41.2 | 81216 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 1148.2 | 186 | X |  |  |  |  | X |  | _ |  |  |  |  | _
295 | X |  |  | 4655 | 2249 | 1289 | 1038 | Water | 53.3919 | 5 | 307.9 | 10 | 51 | 77870 | _ | 2 | 4 | 900 | 660 | 860 | 6.6 | 3 phase 400V/50Hz | 58 | 1435.2 | 233 | X |  |  |  |  | X |  | _ |  |  |  |  | _
296 | X |  |  | 6755 | 2249 | 1289 | 1089 | Water | 52.9411 | 5 | 305.3 | 10 | 49.9 | 132510 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 857.8 | 139 | X |  |  |  |  | X |  | _ |  |  |  |  | _
297 | X |  |  | 6755 | 2249 | 1289 | 1110 | Water | 66.3281 | 5 | 382.5 | 10 | 38 | 127034 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1286.7 | 209 | X |  |  |  |  | X |  | _ |  |  |  |  | _
298 | X |  |  | 6755 | 2249 | 1289 | 1207 | Water | 75.536 | 5 | 435.6 | 10 | 64.4 | 121686 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 1715.5 | 278 | X |  |  |  |  | X |  | _ |  |  |  |  | _
299 | X |  |  | 6755 | 2249 | 1289 | 1296 | Water | 79.8712 | 5 | 460.6 | 10 | 47.5 | 116644 | _ | 2 | 6 | 900 | 660 | 860 | 9.9 | 3 phase 400V/50Hz | 60 | 2144.4 | 348 | X |  |  |  |  | X |  | _ |  |  |  |  | _
300 | X |  |  | 8855 | 2249 | 1289 | 1349 | Water | 69.987 | 5 | 403.6 | 10 | 36.7 | 176632 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1141.4 | 185 | X |  |  |  |  | X |  | _ |  |  |  |  | _
301 | X |  |  | 8855 | 2249 | 1289 | 1492 | Water | 87.6224 | 5 | 505.3 | 10 | 26.6 | 169305 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 1712.1 | 278 | X |  |  |  |  | X |  | _ |  |  |  |  | _
302 | X |  |  | 8855 | 2249 | 1289 | 1587 | Water | 100.6453 | 5 | 580.4 | 10 | 65 | 162155 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 2282.8 | 370 | X |  |  |  |  | X |  | _ |  |  |  |  | _
303 | X |  |  | 8855 | 2249 | 1289 | 1705 | Water | 106.333 | 5 | 613.2 | 10 | 45.8 | 155417 | _ | 2 | 8 | 900 | 660 | 860 | 13.2 | 3 phase 400V/50Hz | 61 | 2853.5 | 463 | X |  |  |  |  | X |  | _ |  |  |  |  | _
304 | X |  |  | 10955 | 2249 | 1289 | 1686 | Water | 90.1715 | 5 | 520 | 10 | 71.4 | 226800 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 1425.1 | 231 | X |  |  |  |  | X |  | _ |  |  |  |  | _
305 | X |  |  | 10955 | 2249 | 1289 | 1961 | Water | 111.1538 | 5 | 641 | 10 | 50.7 | 211577 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 2137.6 | 347 | X |  |  |  |  | X |  | _
306 | X |  |  | 10955 | 2249 | 1289 | 2158 | Water | 124.4367 | 5 | 717.6 | 10 | 37 | 202624 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 2850.2 | 462 | X |  |  |  |  | X |  | _
307 | X |  |  | 10955 | 2249 | 1289 | 2318 | Water | 131.7545 | 5 | 759.8 | 10 | 27.5 | 194190 | _ | 2 | 10 | 900 | 660 | 860 | 16.5 | 3 phase 400V/50Hz | 62 | 3562.7 | 578 | X |  |  |  |  | X |  | _
308 | X |  |  | 4655 | 2249 | 1278 | 987 | Water | 29.6352 | 5 | 170.9 | 10 | 55.6 | 65708 | _ | 2 | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 574.1 | 93 | X |  |  |  |  | X |  | _
309 | X |  |  | 4655 | 2249 | 1278 | 903 | Water | 34.6987 | 5 | 200.1 | 10 | 56.7 | 58675 | _ | 2 | 4 | 1000 | 250 | 380 | 2.68 | 3 phase 400V/50Hz | 43 | 861.1 | 140 | X |  |  |  |  | X |  | _
310 | X |  |  | 6755 | 2249 | 1278 | 1089 | Water | 43.9239 | 5 | 253.3 | 10 | 35.9 | 98422 | _ | 2 | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 857.8 | 139 | X |  |  |  |  | X |  | _
311 | X |  |  | 6755 | 2249 | 1278 | 1110 | Water | 51.8833 | 5 | 299.2 | 10 | 54.9 | 87810 | _ | 2 | 6 | 1000 | 250 | 380 | 4.02 | 3 phase 400V/50Hz | 45 | 1286.7 | 209 | X |  |  |  |  | X |  | _
312 | X |  |  | 8855 | 2249 | 1278 | 1300 | Water | 58.0739 | 5 | 334.9 | 10 | 26.4 | 131134 | _ | 2 | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 1141.4 | 185 | X |  |  |  |  | X |  | _
313 | X |  |  | 8855 | 2249 | 1278 | 1438 | Water | 69.0679 | 5 | 398.3 | 10 | 54 | 116944 | _ | 2 | 8 | 1000 | 250 | 380 | 5.36 | 3 phase 400V/50Hz | 46 | 1712.1 | 278 | X |  |  |  |  | X |  | _
314 | X |  |  | 10955 | 2249 | 1278 | 1625 | Water | 73.6112 | 5 | 424.5 | 10 | 49.8 | 163847 | _ | 2 | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 1425.1 | 231 | X |  |  |  |  | X |  | _
315 | X |  |  | 10955 | 2249 | 1278 | 1890 | Water | 85.4549 | 5 | 492.8 | 10 | 31.8 | 146077 | _ | 2 | 10 | 1000 | 250 | 380 | 6.7 | 3 phase 400V/50Hz | 47 | 2137.6 | 347 | X |  |  |  |  | X |  | _
316 | X | X |  | 2000 | 1590 | 1650 | 240 | Water | 6.3987 | 5 | 36.9 | 10 |  | 10044 | 30 | 1 | 1 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 33 | 160 | 30 | X |  |  |  |  | X |  | 4832 |  |  | X |  | 4994 | 162
317 | X | X |  | 2000 | 1590 | 1650 | 260 | Water | 6.6588 | 5 | 38.4 | 10 |  | 9360 | 30 | 1 | 1 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 33 | 213 | 40 | X |  |  |  |  | X |  | 5338 |  |  | X |  | 5500 | 162
318 | X | X |  | 2400 | 1590 | 1650 | 320 | Water | 7.5085 | 5 | 43.3 | 10 |  | 10332 | 30 | 1 | 1 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 33 | 274 | 50 | X |  |  |  |  | X |  | 5737 |  |  | X |  | 5899 | 162
319 | X | X |  | 3400 | 1590 | 1650 | 480 | Water | 12.7974 | 5 | 73.8 | 10 |  | 20124 | 60 | 1 | 2 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 36 | 320 | 50 | X |  |  |  |  | X |  | 8803 |  |  | X |  | 9051 | 248
320 | X | X |  | 3400 | 1590 | 1650 | 520 | Water | 13.3176 | 5 | 76.8 | 10 |  | 18756 | 60 | 1 | 2 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 36 | 426 | 70 | X |  |  |  |  | X |  | 9768 |  |  | X |  | 10016 | 248
321 | X | X |  | 4200 | 1590 | 1650 | 640 | Water | 15.017 | 5 | 86.6 | 10 |  | 20700 | 60 | 1 | 2 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 36 | 548 | 90 | X |  |  |  |  | X |  | 10708 |  |  | X |  | 10956 | 248
322 | X | X |  | 4800 | 1590 | 1650 | 720 | Water | 19.4216 | 5 | 112 | 10 |  | 30168 | 90 | 1 | 3 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 37 | 480 | 80 | X |  |  |  |  | X |  | 12090 |  |  | X |  | 12425 | 335
323 | X | X |  | 4800 | 1590 | 1650 | 780 | Water | 19.9418 | 5 | 115 | 10 |  | 28116 | 90 | 1 | 3 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 37 | 640 | 100 | X |  |  |  |  | X |  | 13442 |  |  | X |  | 13777 | 335
324 | X | X |  | 6000 | 1590 | 1650 | 960 | Water | 22.5429 | 5 | 130 | 10 |  | 31032 | 90 | 1 | 3 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 37 | 822 | 130 | X |  |  |  |  | X |  | 14877 |  |  | X |  | 15212 | 335
325 | X | X |  | 6200 | 1590 | 1650 | 960 | Water | 25.8376 | 5 | 149 | 10 |  | 40320 | 120 | 1 | 4 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 39 | 640 | 100 | X |  |  |  |  | X |  | 15471 |  |  | X |  | 15903 | 432
326 | X | X |  | 6200 | 1590 | 1650 | 1040 | Water | 26.7046 | 5 | 154 | 10 |  | 37440 | 120 | 1 | 4 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 39 | 852 | 140 | X |  |  |  |  | X |  | 17282 |  |  | X |  | 17714 | 432
327 | X | X |  | 7800 | 1590 | 1650 | 1280 | Water | 29.9994 | 5 | 173 | 10 |  | 41400 | 120 | 1 | 4 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 39 | 1100 | 170 | X |  |  |  |  | X |  | 19117 |  |  | X |  | 19549 | 432
328 | X | X |  | 7600 | 1590 | 1650 | 1200 | Water | 32.2537 | 5 | 186 | 10 |  | 50400 | 156 | 1 | 5 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 40 | 800 | 130 | X |  |  |  |  | X |  | 18746 |  |  | X |  | 19275 | 529
329 | X | X |  | 7600 | 1590 | 1650 | 1300 | Water | 33.4675 | 5 | 193 | 10 |  | 46800 | 156 | 1 | 5 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 40 | 1070 | 170 | X |  |  |  |  | X |  | 20851 |  |  | X |  | 21380 | 529
330 | X | X |  | 9600 | 1590 | 1650 | 1600 | Water | 37.4559 | 5 | 216 | 10 |  | 51840 | 156 | 1 | 5 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 40 | 1370 | 210 | X |  |  |  |  | X |  | 23274 |  |  | X |  | 23803 | 529
331 | X | X |  | 4200 | 2400 | 1700 | 920 | Water | 25.3174 | 5 | 146 | 10 |  | 39600 | 120 | 2 | 2 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 39 | 616 | 100 | X |  |  |  |  | X |  | 16026 |  |  | X |  | 16458 | 432
332 | X | X |  | 4200 | 2400 | 1700 | 990 | Water | 26.3578 | 5 | 152 | 10 |  | 36720 | 120 | 2 | 2 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 39 | 822 | 140 | X |  |  |  |  | X |  | 17826 |  |  | X |  | 18258 | 432
333 | X | X |  | 4800 | 2400 | 1700 | 1110 | Water | 28.2653 | 5 | 163 | 10 |  | 39240 | 120 | 2 | 2 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 39 | 960 | 150 | X |  |  |  |  | X |  | 18908 |  |  | X |  | 19340 | 432
334 | X | X |  | 6000 | 2400 | 1700 | 1370 | Water | 37.9761 | 5 | 219 | 10 |  | 59400 | 186 | 2 | 3 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 41 | 924 | 150 | X |  |  |  |  | X |  | 21975 |  |  | X |  | 22634 | 659
335 | X | X |  | 6000 | 2400 | 1700 | 1490 | Water | 39.1899 | 5 | 226 | 10 |  | 55440 | 186 | 2 | 3 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 41 | 1230 | 200 | X |  |  |  |  | X |  | 24433 |  |  | X |  | 25092 | 659
336 | X | X |  | 6900 | 2400 | 1700 | 1670 | Water | 42.4847 | 5 | 245 | 10 |  | 59040 | 186 | 2 | 3 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 41 | 1440 | 230 | X |  |  |  |  | X |  | 26056 |  |  | X |  | 26715 | 659
337 | X | X |  | 7800 | 2400 | 1700 | 1830 | Water | 50.8082 | 5 | 293 | 10 |  | 79200 | 246 | 2 | 4 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 42 | 1230 | 200 | X |  |  |  |  | X |  | 28136 |  |  | X |  | 29043 | 907
338 | X | X |  | 7800 | 2400 | 1700 | 1980 | Water | 52.5423 | 5 | 303 | 10 |  | 73800 | 246 | 2 | 4 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 42 | 1640 | 260 | X |  |  |  |  | X |  | 31311 |  |  | X |  | 32218 | 907
339 | X | X |  | 9000 | 2400 | 1700 | 2200 | Water | 56.5306 | 5 | 326 | 10 |  | 78840 | 246 | 2 | 4 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 42 | 1920 | 300 | X |  |  |  |  | X |  | 33487 |  |  | X |  | 34394 | 907
340 | X | X |  | 9600 | 2400 | 1700 | 2280 | Water | 63.1201 | 5 | 364 | 10 |  | 99000 | 306 | 2 | 5 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 43 | 1540 | 240 | X |  |  |  |  | X |  | 34309 |  |  | X |  | 35411 | 1102
341 | X | X |  | 9600 | 2400 | 1700 | 2470 | Water | 65.7212 | 5 | 379 | 10 |  | 92160 | 306 | 2 | 5 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 43 | 2060 | 320 | X |  |  |  |  | X |  | 38178 |  |  | X |  | 39280 | 1102
342 | X | X |  | 11100 | 2400 | 1700 | 2770 | Water | 71.0968 | 5 | 410 | 10 |  | 98640 | 306 | 2 | 5 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 43 | 2400 | 370 | X |  |  |  |  | X |  | 40907 |  |  | X |  | 42009 | 1102
343 | X | X |  | 11400 | 2400 | 1700 | 2730 | Water | 76.1256 | 5 | 439 | 10 |  | 119160 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 1850 | 290 | X |  |  |  |  | X |  | 40624 |  |  | X |  | 41920 | 1296
344 | X | X |  | 11400 | 2400 | 1700 | 2970 | Water | 78.3799 | 5 | 452 | 10 |  | 110520 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 2470 | 380 | X |  |  |  |  | X |  | 45210 |  |  | X |  | 46506 | 1296
345 | X | X |  | 13200 | 2400 | 1700 | 3320 | Water | 84.7959 | 5 | 489 | 10 |  | 118080 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 2880 | 450 | X |  |  |  |  | X |  | 48503 |  |  | X |  | 49799 | 1296
346 | X | X |  | 11400 | 2400 | 1700 | 3200 | Water | 78.0331 | 5 | 450 | 10 |  | 103320 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 3080 | 480 | X |  |  |  |  | X |  | 52202 |  |  | X |  | 53498 | 1296
347 | X | X |  | 11400 | 2400 | 1700 | 3430 | Water | 75.6054 | 5 | 436 | 10 |  | 97200 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 3700 | 570 | X |  |  |  |  | X |  | 54936 |  |  | X |  | 56232 | 1296
348 | X | X |  | 13200 | 2400 | 1700 | 3590 | Water | 84.4491 | 5 | 487 | 10 |  | 111600 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 3600 | 550 | X |  |  |  |  | X |  | 56070 |  |  | X |  | 57366 | 1296
349 | X | X |  | 13200 | 2400 | 1700 | 3860 | Water | 82.715 | 5 | 477 | 10 |  | 105840 | 366 | 2 | 6 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 4320 | 660 | X |  |  |  |  | X |  | 59180 |  |  | X |  | 60476 | 1296
350 | X | X |  | 13200 | 2400 | 1700 | 3190 | Water | 89.3045 | 5 | 515 | 10 |  | 138960 | 426 | 2 | 7 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 2160 | 340 | X |  |  |  |  | X |  | 46785 |  |  | X |  | 48297 | 1512
351 | X | X |  | 13200 | 2400 | 1700 | 3460 | Water | 91.7322 | 5 | 529 | 10 |  | 128880 | 426 | 2 | 7 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 2880 | 450 | X |  |  |  |  | X |  | 52100 |  |  | X |  | 53612 | 1512
352 | X | X |  | 13200 | 2400 | 1700 | 3730 | Water | 90.6917 | 5 | 523 | 10 |  | 120600 | 426 | 2 | 7 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 3600 | 550 | X |  |  |  |  | X |  | 59691 |  |  | X |  | 61203 | 1512
353 | X | X |  | 13200 | 2400 | 1700 | 4000 | Water | 88.4375 | 5 | 510 | 10 |  | 113400 | 426 | 2 | 7 | 914 | _ | 350 | _ | 3 phase 400V/50Hz | 44 | 4320 | 660 | X |  |  |  |  | X |  | 62836 |  |  | X |  | 64348 | 1512
354 | X |  |  | 1219.2 | 1009.7 | 1028.7 | 149.7 | Glycol (40%) - water | _ | _ | 62 | _ | _ | _ | _ | 1 | 1 | 609.6 | _ | 1140 | _ | 3 phase 400V/50Hz | _ | _ | _ | X |  |  |  |  | X |  | _
355 | X |  |  | 1308 | 1107 | 1095 | 143 | Water or glycol (40%)-water | _ | 5 | 30 | _ | _ | 4078 | _ | _ |  | _ | _ | 515 | _ | 3 phase 400V/50Hz | 69.5 | _ | _ | X |  |  |  |  | X |  | _
356 | X |  |  | 820 | 1336 | 1030 | 47 | Water or glycol (40%)-water | 1.9 | 5 | 10.8 | 5 | 42 | 7100 | _ | _ | 1 | _ | _ | _ | 0.78 | 1 phase 230V/50 Hz | 46 | _ | _ | X |  |  |  |  | X |  | _
357 | X |  |  | 820 | 1336 | 1030 | 53 | Water or glycol (40%)-water | 2.2 | 5 | 12.8 | 5 | 54 | 6700 | _ | _ | 1 | _ | _ | _ | 0.78 | 1 phase 230V/50 Hz | 46 | _ | _ | X |  |  |  |  | X |  | _
358 | X |  |  | 820 | 2236 | 1030 | 82 | Water or glycol (40%)-water | 2.8 | 5 | 16.1 | 5 | 27 | 15000 | _ | _ | 2 | _ | _ | _ | 1.56 | 1 phase 230V/50 Hz | 49 | _ | _ | X |  |  |  |  | X |  | _
359 | X |  |  | 820 | 2236 | 1030 | 94 | Water or glycol (40%)-water | 3.8 | 5 | 22 | 5 | 52 | 14200 | _ | _ | 2 | _ | _ | _ | 1.56 | 1 phase 230V/50 Hz | 49 | _ | _ | X |  |  |  |  | X |  | _
360 | X |  |  | 1250 | 2866 | 1070 | 133 | Water or glycol (40%)-water | 4.9 | 5 | 28 | 5 | 40 | 20000 | _ | _ | 2 | _ | _ | _ | 1.38 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X |  | _
361 | X |  |  | 1250 | 2866 | 1070 | 153 | Water or glycol (40%)-water | 6.3 | 5 | 36.4 | 5 | 31 | 19400 | _ | _ | 2 | _ | _ | _ | 1.38 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X |  | _
362 | X |  |  | 1250 | 2866 | 1070 | 193 | Water or glycol (40%)-water | 8 | 5 | 46.1 | 5 | 43 | 18400 | _ | _ | 2 | _ | _ | _ | 1.38 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X |  | _
363 | X |  |  | 1250 | 2866 | 1070 | 254 | Water or glycol (40%)-water | 10.9 | 5 | 62.8 | 5 | 22 | 28200 | _ | _ | 3 | _ | _ | _ | 2.07 | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  |  | X |  | _
364 | X |  |  | 1250 | 2866 | 1070 | 283 | Water or glycol (40%)-water | 12.1 | 5 | 69.5 | 5 | 55 | 27600 | _ | _ | 3 | _ | _ | _ | 2.07 | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  |  | X |  | _
365 | X |  |  | 1250 | 2866 | 1070 | 340 | Water or glycol (40%)-water | 14.7 | 5 | 84.8 | 5 | 48 | 37600 | _ | _ | 4 | _ | _ | _ | 2.76 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X |  | _
366 | X |  |  | 1620 | 5276 | 1650 | 763 | Water or glycol (40%)-water | 22.4 | 5 | 128.9 | 5 | 58 | 63000 | _ | _ | 3 | _ | _ | _ | 6 | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  |  | X |  | _
367 | X |  |  | 1620 | 6826 | 1650 | 990 | Water or glycol (40%)-water | 29.2 | 5 | 168.1 | 5 | 17 | 84000 | _ | _ | 4 | _ | _ | _ | 8 | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  |  | X |  | _
368 | X |  |  | 2340 | 5576 | 1650 | 1115 | Water or glycol (40%)-water | 37.8 | 5 | 217.6 | 5 | 11 | 118800 | _ | _ | 6 | _ | _ | _ | 12 | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  |  | X |  | _
369 | X |  |  | 2340 | 5576 | 1650 | 1253 | Water or glycol (40%)-water | 46.1 | 5 | 265.4 | 5 | 54 | 109200 | _ | _ | 6 | _ | _ | _ | 12 | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  |  | X |  | _
370 | X |  |  | 2340 | 7266 | 1650 | 1585 | Water or glycol (40%)-water | 56.9 | 5 | 327.2 | 5 | 20 | 151600 | _ | _ | 8 | _ | _ | _ | 16 | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  |  | X |  | _
371 | X |  |  | 2340 | 8876 | 1650 | 1940 | Water or glycol (40%)-water | 72 | 5 | 414.1 | 5 | 38 | 189500 | _ | _ | 10 | _ | _ | _ | 20 | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  |  | X |  | _
372 | X |  |  | 2550 | 1260 | 990 | 200 | glycol (35%) - Water | 7.236 | 5 | 39 | 8 | 38 | 21600 | _ | _ | 2 | 630 | _ | 870 | 1.4 | 3 phase 400V/50Hz | 55 | _ | 14 | X |  |  |  |  | X |  | _
373 | X |  |  | 2550 | 1260 | 990 | 210 | glycol (35%) - Water | 9.108 | 5 | 49 | 8 | 26 | 20199.6 | _ | _ | 2 | 630 | _ | 870 | 1.4 | 3 phase 400V/50Hz | 55 | _ | 21 | X |  |  |  |  | X |  | _
374 | X |  |  | 3700 | 1260 | 990 | 275 | glycol (35%) - Water | 10.584 | 5 | 57 | 8 | 14 | 32400 | _ | _ | 3 | 630 | _ | 870 | 2.2 | 3 phase 400V/50Hz | 57 | _ | 21 | X |  |  |  |  | X |  | _
375 | X |  |  | 3700 | 1260 | 990 | 300 | glycol (35%) - Water | 13.392 | 5 | 72 | 8 | 12 | 30301.2 | _ | _ | 3 | 630 | _ | 870 | 2.2 | 3 phase 400V/50Hz | 57 | _ | 31 | X |  |  |  |  | X |  | _
376 | X |  |  | 3700 | 1260 | 990 | 340 | glycol (35%) - Water | 16.524 | 5 | 89 | 8 | 12 | 30301.2 | _ | _ | 3 | 630 | _ | 870 | 2.2 | 3 phase 400V/50Hz | 57 | _ | 41 | X |  |  |  |  | X |  | _
377 | X |  |  | 3310 | 1640 | 1200 | 310 | glycol (35%) - Water | 16.92 | 5 | 91 | 8 | 50 | 37501.2 | _ | _ | 2 | 800 | _ | 900 | 2.9 | 3 phase 400V/50Hz | 57 | _ | 36 | X |  |  |  |  | X |  | _
378 | X |  |  | 4880 | 1260 | 990 | 380 | glycol (35%) - Water | 18.396 | 5 | 99 | 8 | 25 | 40399.2 | _ | _ | 4 | 630 | _ | 870 | 2.9 | 3 phase 400V/50Hz | 58 | _ | 41 | X |  |  |  |  | X |  | _
379 | X |  |  | 3330 | 1640 | 1200 | 360 | glycol (35%) - Water | 19.692 | 5 | 106 | 8 | 40 | 36298.8 | _ | _ | 2 | 800 | _ | 900 | 2.9 | 3 phase 400V/50Hz | 57 | _ | 49 | X |  |  |  |  | X |  | _
380 | X |  |  | 4880 | 1260 | 990 | 440 | glycol (35%) - Water | 21.564 | 5 | 116 | 8 | 18 | 39600 | _ | _ | 4 | 630 | _ | 870 | 2.9 | 3 phase 400V/50Hz | 58 | _ | 55 | X |  |  |  |  | X |  | _
381 | X |  |  | 4830 | 1640 | 1500 | 440 | glycol (35%) - Water | 24.876 | 5 | 134 | 8 | 23 | 56199.6 | _ | _ | 3 | 800 | _ | 900 | 4.4 | 3 phase 400V/50Hz | 59 | _ | 55 | X |  |  |  |  | X |  | _
382 | X |  |  | 4840 | 1640 | 1500 | 510 | glycol (35%) - Water | 28.98 | 5 | 156 | 8 | 17 | 54399.6 | _ | _ | 3 | 800 | _ | 900 | 4.4 | 3 phase 400V/50Hz | 59 | _ | 73 | X |  |  |  |  | X |  | _
383 | X |  |  | 6340 | 1640 | 1500 | 580 | glycol (35%) - Water | 33.984 | 5 | 183 | 8 | 48 | 74998.8 | _ | _ | 4 | 800 | _ | 900 | 5.8 | 3 phase 400V/50Hz | 60 | _ | 73 | X |  |  |  |  | X |  | _
384 | X |  |  | 6375 | 1640 | 1500 | 670 | glycol (35%) - Water | 39.384 | 5 | 212 | 8 | 36 | 72500.4 | _ | _ | 4 | 800 | _ | 900 | 5.8 | 3 phase 400V/50Hz | 60 | _ | 97 | X |  |  |  |  | X |  | _
385 | X |  |  | 4605 | 2420 | 1500 | 690 | glycol (35%) - Water | 41.796 | 5 | 225 | 8 | 65 | 100501.2 | _ | _ | 6 | 800 | _ | 900 | 8.7 | 3 phase 400V/50Hz | 62 | _ | 137 | X |  |  |  |  | X |  | _
386 | X |  |  | 3805 | 2440 | 1770 | 830 | glycol (35%) - Water | 44.388 | 5 | 239 | 8 | 81 | 94399.2 | _ | _ | 4 | 1000 | _ | 670 | 8.8 | 3 phase 400V/50Hz | 62 | _ | 89 | X |  |  |  |  | X |  | _
387 | X |  |  | 6375 | 1640 | 1570 | 705 | glycol (35%) - Water | 47.916 | 5 | 258 | 8 | 52 | 101998.8 | _ | _ | 4 | 900 | _ | 850 | 13.2 | 3 phase 400V/50Hz | 64 | _ | 97 | X |  |  |  |  | X |  | _
388 | X |  |  | 1000 | 1000 | 950 | 110 | Water | 1.56 | 5 | 9 | 5 | _ | 13800 | _ | _ | 1 | 630 | _ | _ | 1.6 | 3 phase 230/400V - 50Hz - 4 poli | 58 | 37.1 | 8 | X |  |  |  |  | X |  | _
389 | X |  |  | 1000 | 1000 | 950 | 120 | Water | 2.2 | 5 | 13 | 5 | _ | 13200 | _ | _ | 1 | 630 | _ | _ | 1.6 | 3 phase 230/400V - 50Hz - 4 poli | 58 | 55.7 | 13 | X |  |  |  |  | X |  | _
390 | X |  |  | 1000 | 1000 | 950 | 130 | Water | 2.74 | 5 | 16 | 5 | _ | 12200 | _ | _ | 1 | 630 | _ | _ | 1.6 | 3 phase 230/400V - 50Hz - 4 poli | 58 | 74.3 | 16 | X |  |  |  |  | X |  | _
391 | X |  |  | 1000 | 1000 | 950 | 140 | Water | 3.08 | 5 | 18 | 5 | _ | 11400 | _ | _ | 1 | 630 | _ | _ | 1.6 | 3 phase 230/400V - 50Hz - 4 poli | 58 | 92.8 | 19 | X |  |  |  |  | X |  | _
392 | X |  |  | 2000 | 1000 | 950 | 210 | Water | 4.6 | 5 | 27 | 5 | _ | 26400 | _ | _ | 2 | 630 | _ | _ | 3.2 | 3 phase 230/400V - 50Hz - 4 poli | 61 | 119 | 22 | X |  |  |  |  | X |  | _
393 | X |  |  | 2000 | 1000 | 950 | 220 | Water | 5.6 | 5 | 33 | 5 | _ | 24000 | _ | _ | 2 | 630 | _ | _ | 3.2 | 3 phase 230/400V - 50Hz - 4 poli | 61 | 158.6 | 28 | X |  |  |  |  | X |  | _
394 | X |  |  | 2000 | 1000 | 950 | 250 | Water | 6.4 | 5 | 37 | 5 | _ | 22800 | _ | _ | 2 | 630 | _ | _ | 3.2 | 3 phase 230/400V - 50Hz - 4 poli | 61 | 198.3 | 51 | X |  |  |  |  | X |  | _
395 | X |  |  | 3000 | 1000 | 950 | 290 | Water | 7 | 5 | 41 | 5 | _ | 39600 | _ | _ | 3 | 630 | _ | _ | 4.8 | 3 phase 230/400V - 50Hz - 4 poli | 62 | 182.3 | 33 | X |  |  |  |  | X |  | _
396 | X |  |  | 3000 | 1000 | 950 | 330 | Water | 8.2 | 5 | 48 | 5 | _ | 36300 | _ | _ | 3 | 630 | _ | _ | 4.8 | 3 phase 230/400V - 50Hz - 4 poli | 62 | 243 | 42 | X |  |  |  |  | X |  | _
397 | X |  |  | 3000 | 1000 | 950 | 360 | Water | 9.8 | 5 | 57 | 5 | _ | 34200 | _ | _ | 3 | 630 | _ | _ | 4.8 | 3 phase 230/400V - 50Hz - 4 poli | 62 | 303.8 | 51 | X |  |  |  |  | X |  | _
398 | X |  |  | 2000 | 2000 | 950 | 400 | Water | 9.2 | 5 | 53 | 5 | _ | 52800 | _ | _ | 4 | 630 | _ | _ | 6.4 | 3 phase 230/400V - 50Hz - 4 poli | 64 | 237.9 | 46 | X |  |  |  |  | X |  | _
399 | X |  |  | 2000 | 2000 | 950 | 430 | Water | 11.2 | 5 | 65 | 5 | _ | 48800 | _ | _ | 4 | 630 | _ | _ | 6.4 | 3 phase 230/400V - 50Hz - 4 poli | 64 | 317.3 | 58 | X |  |  |  |  | X |  | _
400 | X |  |  | 2000 | 2000 | 950 | 480 | Water | 12.6 | 5 | 73 | 5 | _ | 45600 | _ | _ | 4 | 630 | _ | _ | 6.4 | 3 phase 230/400V - 50Hz - 4 poli | 64 | 396.6 | 77 | X |  |  |  |  | X |  | _
401 | X |  |  | 2000 | 2000 | 950 | 520 | Water | 15.2 | 5 | 88 | 5 | _ | 44000 | _ | _ | 4 | 630 | _ | _ | 6.4 | 3 phase 230/400V - 50Hz - 4 poli | 64 | 475.9 | 89 | X |  |  |  |  | X |  | _
402 | X |  |  | 3000 | 2000 | 1070 | 710 | Water | 16.6 | 5 | 97 | 5 | _ | 73200 | _ | _ | 6 | 630 | _ | _ | 9.6 | 3 phase 230/400V - 50Hz - 4 poli | 65 | 486 | 89 | X |  |  |  |  | X |  | _
403 | X |  |  | 3000 | 2000 | 1070 | 800 | Water | 19.2 | 5 | 112 | 5 | _ | 68400 | _ | _ | 6 | 630 | _ | _ | 9.6 | 3 phase 230/400V - 50Hz - 4 poli | 65 | 607.5 | 113 | X |  |  |  |  | X |  | _
404 | X |  |  | 4000 | 2000 | 1070 | 890 | Water | 20 | 5 | 116 | 5 | _ | 105600 | _ | _ | 8 | 630 | _ | _ | 12.8 | 3 phase 230/400V - 50Hz - 4 poli | 67 | 491.1 | 95 | X |  |  |  |  | X |  | _
405 | X |  |  | 4000 | 2000 | 1070 | 970 | Water | 23 | 5 | 134 | 5 | _ | 97600 | _ | _ | 8 | 630 | _ | _ | 12.8 | 3 phase 230/400V - 50Hz - 4 poli | 67 | 654.8 | 119 | X |  |  |  |  | X |  | _
406 | X |  |  | 4000 | 2000 | 1070 | 1060 | Water | 26 | 5 | 151 | 5 | _ | 91200 | _ | _ | 8 | 630 | _ | _ | 12.8 | 3 phase 230/400V - 50Hz - 4 poli | 67 | 818.5 | 159 | X |  |  |  |  | X |  | _
407 | X |  |  | 4000 | 2000 | 1070 | 1150 | Water | 31 | 5 | 180 | 5 | _ | 88000 | _ | _ | 8 | 630 | _ | _ | 12.8 | 3 phase 230/400V - 50Hz - 4 poli | 67 | 982.2 | 183 | X |  |  |  |  | X |  | _
408 | X |  |  | 2000 | 2000 | 1010 | 690 | Water | 16 | 5 | 93 | 5 | _ | 43000 | _ | _ | 4 | 710 | _ | _ | 8.8 | 3 phase 230/400V - 50Hz - 4 poli | 68 | 634.5 | 112 | X |  |  |  |  | X |  | _
409 | X |  |  | 3000 | 2000 | 1130 | 990 | Water | 24 | 5 | 140 | 5 | _ | 64500 | _ | _ | 6 | 710 | _ | _ | 13.2 | 3 phase 230/400V - 50Hz - 4 poli | 69 | 972 | 167 | X |  |  |  |  | X |  | _
410 | X |  |  | 4000 | 2000 | 1130 | 1320 | Water | 31.6 | 5 | 184 | 5 | _ | 86000 | _ | _ | 8 | 710 | _ | _ | 17.6 | 3 phase 230/400V - 50Hz - 4 poli | 71 | 1309.5 | 232 | X |  |  |  |  | X |  | _
411 | X |  |  | 1350 | 1910 | 2065 | 500 | Water | 10.3 | 5 | 82 | 10 | 24 | 26000 | _ | 1 | 1 | 910 | _ | _ | 2.25 | _ | 47 | _ | _ | X |  |  |  |  | X |  | _
412 | X |  |  | 2500 | 1910 | 2065 | 800 | Water | 20.5 | 5 | 169 | 10 | 44 | 52000 | _ | 1 | 2 | 910 | _ | _ | 4.5 | _ | 56.5 | _ | _ | X |  |  |  |  | X |  | _
413 | X |  |  | 3650 | 1910 | 2065 | 1200 | Water | 34.6 | 5 | 282 | 10 | 32 | 76000 | _ | 1 | 3 | 910 | _ | _ | 6.75 | _ | 52 | _ | _ | X |  |  |  |  | X |  | _
414 | X |  |  | 1350 | 1600 | 2065 | 450 | Water | 10.8 | 5 | 63 | 10 | 26 | 27500 | _ | 1 | 1 | 910 | _ | _ | 2.25 | _ | 47 | _ | _ | X |  |  |  |  | X |  | _
415 | X |  |  | 570 | _ | 620 | 24 | Water | _ | _ | 6.6 | _ | _ | 2628 | _ | 1 | 1 | _ | _ |  | 0.15 | _ | 39 | _ | _ | X |  |  |  |  | X |  | _
416 | X |  |  | 1120 | 100 | 1170 | 39 | Water | _ | _ | 13.2 | _ | _ | 5220 | _ | 1 | 2 | _ | _ |  | 0.3 | _ | 42 | _ | _ | X |  |  |  |  | X |  | _
417 | X |  |  | 1670 | 650 | 1720 | 64 | Water | _ | _ | 26.2 | _ | _ | 6768 | _ | 1 | 3 | _ | _ |  | 0.45 | _ | 44 | _ | _ | X |  |  |  |  | X |  | _
418 | X |  |  | 893 | 898 | 997 | 85 | R404A | _ | _ | 16.3 | _ | _ | 6840 | _ | _ | 1 | 500 | _ | 1225 | 0.54 | 1 phase 4 poli | 45 | _ | _ | X |  |  |  |  | X |  | _
419 | X |  |  | 5144 | 898 | 997 | 515 | R404A | _ | _ | 115.2 | _ | _ | 27792 | _ | _ | 4 | 500 | _ | 1225 | 2.16 | 1 phase 4 poli | 51 | _ | _ | X |  |  |  |  | X |  | _
420 | X |  |  | 1534 | 898 | 1008 | 113 | R404A | _ | _ | 28.2 | _ | _ | 13536 | _ | _ | 1 | 630 | _ | 1330 | 2.5 | 3 phase 4 poli | 61 | _ | _ | X |  |  |  |  | X |  | _
421 | X |  |  | 2400 | 2200 | 2220 | 770 | glycol (34 %) - water | 43 | 5 | 222 | 10 | 60 | 82400 | _ | 2 | 2 | 800 | 690 | 890 | 6.8 | 3 phase 400V/50Hz | 54 | 661 | _ | X |  |  |  |  | X |  | 17290 |  |  |  |  | 17290
422 | X |  |  | 6000 | 2200 | 2220 | 1850 | glycol (34 %) - water | 106 | 5 | 550 | 10 | 60 | 206000 | _ | 2 | 5 | 800 | 690 | 890 | 17 | 3 phase 400V/50Hz | 58 | 1673 | _ | X |  |  |  |  | X |  | 38533 |  |  |  |  | 38533
423 | X |  |  | 9600 | 2200 | 2220 | 3470 | glycol (34 %) - water | 178 | 5 | 1087 | 10 | 220 | 329600 | _ | 2 | 8 | 800 | 690 | 890 | 27.2 | 3 phase 400V/50Hz | 59 | 4027 | _ | X |  |  |  |  | X |  | 77440 |  |  |  |  | 77440
424 | X |  |  | 925 | 895 | 950 | 96 | glycol (34 %) - water | 4 | 5 | 24.3 | 10 | 100 | 7110 | _ | 2 | _ | 500 | _ | 1250 | 0.7 | 1 phase 230V/50 Hz | 49 | 82 | _ | X |  |  |  |  | X |  | _
425 | X |  |  | 2775 | 895 | 950 | 250 | glycol (34 %) - water | 12.5 | 5 | 74.1 | 10 | 90 | 21700 | _ |  | _ | 500 | _ | 1250 | 2.2 | 1 phase 230V/50 Hz | 53 | 255 | _ | X |  |  |  |  | X |  | _
426 | X |  |  | 925 | 1145 | 950 | 105 | glycol (34 %) - water | 6.5 | 5 | 37.9 | 10 | 70 | 12700 | _ |  | _ | 650 | _ | 1340 | 2 | 3 phase 400V/50Hz | 59 | 108 | _ | X |  |  |  |  | X |  | _
427 | X |  |  | 4500 | 1145 | 950 | 482 | glycol (34 %) - water | 30 | 5 | 179.2 | 10 | 60 | 55800 | _ |  | _ | 650 | _ | 1340 | 7.8 | 3 phase 400V/50Hz | 64 | 547 | _ | X |  |  |  |  | X |  | _
428 | X |  |  | 1850 | 2195 | 1150 | 422 | glycol (34 %) - water | 26.8 | 5 | 155.7 | 10 | 100 | 51500 | _ | 2 | 4 | 650 | _ | 1340 | 8 | 3 phase 400V/50Hz | 64 | 443 | _ | X |  |  |  |  | X |  | _
429 | X |  |  | 2775 | 2195 | 1150 | 589 | glycol (34 %) - water | 40.3 | 5 | 234.2 | 10 | 80 | 77600 | _ | 2 | 6 | 650 | _ | 1340 | 12 | 3 phase 400V/50Hz | 66 | 670 | _ | X |  |  |  |  | X |  | _
430 | X |  |  | 4500 | 2195 | 1150 | 873 | glycol (34 %) - water | 59.9 | 5 | 358.4 | 10 | 60 | 111600 | _ | 2 | 8 | 650 | _ | 1340 | 15.6 | 3 phase 400V/50Hz | 67 | 1095 | _ | X |  |  |  |  | X |  | _
431 | X |  |  | 925 | 895 | 950 | 92 | glycol (34 %) - water | 2.9 | 5 | 17.9 | 10 | 60 | 4750 | _ | _ | _ | 500 | _ | 890 | 0.3 | 1 phase 230V/50 Hz | 39 | 82 | _ | X |  |  |  |  | X |  | _
432 | X |  |  | 1850 | 895 | 950 | 164 | glycol (34 %) - water | 6 | 5 | 36.6 | 10 | 70 | 9620 | _ | _ | _ | 500 | _ | 890 | 0.6 | 1 phase 230V/50 Hz | 42 | 169 | _ | X |  |  |  |  | X |  | _
433 | X |  |  | 2775 | 895 | 950 | 244 | glycol (34 %) - water | 9.1 | 5 | 55.1 | 10 | 50 | 14500 | _ | _ | _ | 500 | _ | 890 | 0.8 | 1 phase 230V/50 Hz | 43 | 255 | _ | X |  |  |  |  | X |  | _
434 | X |  |  | 925 | 1145 | 950 | 101 | glycol (34 %) - water | 5.4 | 5 | 29 | 10 | 90 | 8070 | _ | _ | _ | 650 | _ | 870 | 0.7 | 1 phase 230V/50 Hz | 47 | 108 | _ | X |  |  |  |  | X |  | _
435 | X |  |  | 1850 | 1145 | 950 | 188 | glycol (34 %) - water | 9.6 | 5 | 57.9 | 10 | 60 | 16300 | _ | _ | _ | 650 | _ | 870 | 1.4 | 1 phase 230V/50 Hz | 50 | 221 | _ | X |  |  |  |  | X |  | _
436 | X |  |  | 2775 | 1145 | 950 | 265 | glycol (34 %) - water | 15.2 | 5 | 88.9 | 10 | 80 | 24600 | _ | _ | _ | 650 | _ | 870 | 2 | 1 phase 230V/50 Hz | 51 | 335 | _ | X |  |  |  |  | X |  | _
437 | X |  |  | 1850 | 2195 | 1150 | 417 | glycol (34 %) - water | 19.5 | 5 | 116.5 | 10 | 100 | 32700 | _ | 2 | 4 | 650 | _ | 870 (650 3 phase) | 2.7 | 1 phase - 3 phase | 52 | 443 | _ | X |  |  |  |  | X |  | _
438 | X |  |  | 2775 | 2195 | 1150 | 584 | glycol (34 %) - water | 29.3 | 5 | 177.8 | 10 | 70 | 49200 | _ | 2 | 6 | 650 | _ | 870 (650 3 phase) | 4.1 | 1 phase - 3 phase | 54 | 670 | _ | X |  |  |  |  | X |  | _
439 | X |  |  | 4500 | 2195 | 1150 | 870 | glycol (34 %) - water | 43.5 | 5 | 264.6 | 10 | 70 | 71100 | _ | 2 | 8 | 650 | _ | 870 (650 3 phase) | 5.4 | 1 phase - 3 phase | 55 | 1095 | _ | X |  |  |  |  | X |  | _
440 | X |  |  | 2700 | 1141 | 1430 | _ | Water | 3 | 4 | 14 | 4 | 18 | 10500 | _ |  | 1 | 800 | _ | _ | 0.27 | 1 phase 230V/50Hz EC | 66 | 197.6 | _ | X |  |  |  |  | X |  | 3000 |  | X |  |  | 3850
441 |  | X |  | 2000 | 1145 | 950 | _ | Water | 3.7 | 5 | 21.5 | 2.5 | 15 | 13000 | 20 |  | 2 | _ | _ | _ | 0.65 | 1 phase 230V/50Hz EC | 45 | 221 | _ | X |  |  |  |  | X |  | 4000
442 | X |  |  | 2490 | 1185 | 1660 | 503 | glycol (34 %) - water | 25 | 5 | 132 | 10 | 27 | 42000 | _ |  | 2 | 800 | 690 | 890 | 3.4 | 3 phase 400V/50Hz | 51 | 536 | _ | X |  |  |  |  | X |  | 8397 |  |  |  |  | 8397
443 | X |  |  | 4890 | 1185 | 1660 | 949 | glycol (34 %) - water | 49.3 | 5 | 259 | 10 | 26 | 84000 | _ |  | 4 | 800 | 690 | 890 | 6.8 | 3 phase 400V/50Hz | 54 | 1072 | _ | X |  |  |  |  | X |  | _
444 | X |  |  | 7290 | 1185 | 1660 | 1387 | glycol (34 %) - water | 77.7 | 5 | 410 | 10 | 82 | 126000 | _ |  | 6 | 800 | 690 | 890 | 10.1 | 3 phase 400V/50Hz | 55 | 1609 | _ | X |  |  |  |  | X |  | _
445 | X |  |  | 9690 | 1185 | 1660 | 1829 | glycol (34 %) - water | 92.4 | 5 | 487 | 10 | 22 | 168000 | _ |  | 8 | 800 | 690 | 890 | 13.5 | 3 phase 400V/50Hz | 56 | 2145 | _ | X |  |  |  |  | X |  | _
446 | X |  |  | 2490 | 1185 | 1720 | 537 | glycol (34 %) - water | 32.3 | 5 | 173 | 10 | 44 | 62200 | _ |  | 2 | 900 | 700 | 890 | 7.1 | 3 phase 400V/50Hz | 60 | 536 | _ | X |  |  |  |  | X |  | 9491 |  |  |  |  | 9491
447 | X |  |  | 4890 | 1185 | 1720 | 1015 | glycol (34 %) - water | 63.5 | 5 | 341 | 10 | 42 | 124400 | _ |  | 4 | 900 | 700 | 890 | 14.2 | 3 phase 400V/50Hz | 63 | 1072 | _ | X |  |  |  |  | X |  | 17914 |  |  |  |  | 17914
448 | X |  |  | 7290 | 1185 | 1720 | 1486 | glycol (34 %) - water | 85.2 | 5 | 458 | 10 | 16 | 186600 | _ |  | 6 | 900 | 700 | 890 | 21.3 | 3 phase 400V/50Hz | 64 | 1609 | _ | X |  |  |  |  | X |  | 26306 |  |  |  |  | 26306
449 | X |  |  | 9690 | 1185 | 1720 | 1970 | glycol (34 %) - water | 120.4 | 5 | 647 | 10 | 37 | 248800 | _ |  | 8 | 900 | 700 | 890 | 28.4 | 3 phase 400V/50Hz | 65 | 2145 | _ | X |  |  |  |  | X |  | 34910 |  |  |  |  | 34910
450 | X |  |  | 2490 | 1185 | 1660 | 503 | glycol (34 %) - water | 24.2 | 5 | 128 | 10 | 75 | 37600 | _ |  | 2 | 800 | 530 | 800 | 2.8 | 3 phase 400V/50Hz | 48 | 536 | _ | X |  |  |  |  | X |  | 8397 |  |  |  |  | 8397
451 | X |  |  | 4890 | 1185 | 1660 | 949 | glycol (34 %) - water | 48.1 | 5 | 254 | 10 | 72 | 75200 | _ |  | 4 | 800 | 530 | 800 | 5.5 | 3 phase 400V/50Hz | 51 | 1072 | _ | X |  |  |  |  | X |  | _
452 | X |  |  | 7290 | 1185 | 1660 | 1387 | glycol (34 %) - water | 71.1 | 5 | 376 | 10 | 70 | 112800 | _ |  | 6 | 800 | 530 | 800 | 8.3 | 3 phase 400V/50Hz | 52 | 1609 | _ | X |  |  |  |  | X |  | _
453 | X |  |  | 9690 | 1185 | 1660 | 1829 | glycol (34 %) - water | 83.9 | 5 | 445 | 10 | 19 | 150400 | _ |  | 8 | 800 | 530 | 800 | 11 | 3 phase 400V/50Hz | 53 | 2145 | _ | X |  |  |  |  | X |  | _
454 | X |  |  | 2490 | 1185 | 1720 | 537 | glycol (34 %) - water | 29 | 5 | 156 | 10 | 37 | 53000 | _ |  | 2 | 900 | 550 | 770 | 5.4 | 3 phase 400V/50Hz | 57 | 536 | _ | X |  |  |  |  | X |  | _
455 | X |  |  | 4890 | 1185 | 1720 | 1015 | glycol (34 %) - water | 57.1 | 5 | 307 | 10 | 34 | 106000 | _ |  | 4 | 900 | 550 | 770 | 10.8 | 3 phase 400V/50Hz | 60 | 1072 | _ | X |  |  |  |  | X |  | _
456 | X |  |  | 7290 | 1185 | 1720 | 1486 | glycol (34 %) - water | 90.3 | 5 | 485 | 10 | 110 | 159000 | _ |  | 6 | 900 | 550 | 770 | 16.2 | 3 phase 400V/50Hz | 61 | 1609 | _ | X |  |  |  |  | X |  | 26675.4805 |  |  |  |  | 26675.4805
457 | X |  |  | 9690 | 1185 | 1720 | 1970 | glycol (34 %) - water | 107.7 | 5 | 578 | 10 | 30 | 212000 | _ |  | 8 | 900 | 550 | 770 | 21.6 | 3 phase 400V/50Hz | 62 | 2145 | _ | X |  |  |  |  | X |  | _
458 | X |  |  | 2844 | 2383 | 2500 | 1064 | glycol (34 %) - water | 67.2 | 5 | 359 | 10 | 40 | 120400 | _ |  | 4 | 900 | _ | _ | 13 | 3 phase 400V/50Hz 6 poli EC | 63 | _ | 182 | X | X |  |  |  | X |  | _
459 | X |  |  | 2844 | 2383 | 2500 | 1166 | glycol (34 %) - water | 74 | 5 | 395 | 10 | 31 | 114400 | _ |  | 4 | 900 | _ | _ | 13 | 3 phase 400V/50Hz 6 poli EC | 63 | _ | 218 | X | X |  |  |  | X |  | _
460 | X |  |  | 4266 | 2383 | 2500 | 1533 | glycol (34 %) - water | 101.7 | 5 | 544 | 10 | 46 | 180600 | _ |  | 6 | 900 | _ | _ | 19.5 | 3 phase 400V/50Hz 6 poli EC | 65 | _ | 236 | X | X |  |  |  | X |  | _
461 | X |  |  | 4266 | 2383 | 2500 | 1685 | glycol (34 %) - water | 111.9 | 5 | 599 | 10 | 41 | 171600 | _ |  | 6 | 900 | _ | _ | 19.5 | 3 phase 400V/50Hz 6 poli EC | 65 | _ | 290 | X | X |  |  |  | X |  | _
462 | X |  |  | 5688 | 2383 | 2500 | 1881 | glycol (34 %) - water | 138 | 5 | 738 | 10 | 98 | 240800 | _ |  | 8 | 900 | _ | _ | 26 | 3 phase 400V/50Hz 6 poli EC | 66 | _ | 288 | X | X |  |  |  | X |  | _
463 | X |  |  | 5688 | 2383 | 2500 | 2083 | glycol (34 %) - water | 151.5 | 5 | 810 | 10 | 59 | 228800 | _ |  | 8 | 900 | _ | _ | 26 | 3 phase 400V/50Hz 6 poli EC | 66 | _ | 362 | X | X |  |  |  | X |  | _
464 | X |  |  | 7110 | 2383 | 2500 | 2233 | glycol (34 %) - water | 167.1 | 5 | 894 | 10 | 28 | 301000 | _ |  | 10 | 900 | _ | _ | 32.5 | 3 phase 400V/50Hz 6 poli EC | 67 | _ | 342 | X | X |  |  |  | X |  | _
465 | X |  |  | 2844 | 2383 | 2500 | 1064 | glycol (34 %) - water | 61.4 | 5 | 328 | 10 | 34 | 104400 | _ |  | 4 | 900 | _ | _ | 9 | 3 phase 400V/50Hz 6 poli EC | 57 | _ | 182 | X | X |  |  |  | X |  | _
466 | X |  |  | 2844 | 2383 | 2500 | 1166 | glycol (34 %) - water | 66.7 | 5 | 357 | 10 | 26 | 99600 | _ |  | 4 | 900 | _ | _ | 9 | 3 phase 400V/50Hz 6 poli EC | 57 | _ | 218 | X | X |  |  |  | X |  | _
467 | X |  |  | 4266 | 2383 | 2500 | 1533 | glycol (34 %) - water | 93 | 5 | 497 | 10 | 39 | 156600 | _ |  | 6 | 900 | _ | _ | 13.5 | 3 phase 400V/50Hz 6 poli EC | 59 | _ | 236 | X | X |  |  |  | X |  | _
468 | X |  |  | 4266 | 2383 | 2500 | 1685 | glycol (34 %) - water | 101 | 5 | 540 | 10 | 34 | 149400 | _ |  | 6 | 900 | _ | _ | 13.5 | 3 phase 400V/50Hz 6 poli EC | 59 | _ | 290 | X | X |  |  |  | X |  | _
469 | X |  |  | 5688 | 2383 | 2500 | 1881 | glycol (34 %) - water | 125.9 | 5 | 674 | 10 | 83 | 208800 | _ |  | 8 | 900 | _ | _ | 18 | 3 phase 400V/50Hz 6 poli EC | 60 | _ | 288 | X | X |  |  |  | X |  | _
470 | X |  |  | 5688 | 2383 | 2500 | 2083 | glycol (34 %) - water | 136.7 | 5 | 731 | 10 | 49 | 199200 | _ |  | 8 | 900 | _ | _ | 18 | 3 phase 400V/50Hz 6 poli EC | 60 | _ | 362 | X | X |  |  |  | X |  | _
471 | X |  |  | 7110 | 2383 | 2500 | 2233 | glycol (34 %) - water | 152.8 | 5 | 817 | 10 | 23 | 261000 | _ |  | 10 | 900 | _ | _ | 22.5 | 3 phase 400V/50Hz 6 poli EC | 61 | _ | 342 | X | X |  |  |  | X |  | _
472 | X |  |  | 2844 | 2383 | 2500 | 1064 | glycol (34 %) - water | 53.7 | 5 | 287 | 10 | 64 | 84000 | _ |  | 4 | 800 | _ | _ | 6.56 | 3 phase 400V/50Hz 6 poli EC | 53 | _ | 182 | X | X |  |  |  | X |  | _
473 | X |  |  | 2844 | 2383 | 2500 | 1166 | glycol (34 %) - water | 57.4 | 5 | 307 | 10 | 50 | 80400 | _ |  | 4 | 800 | _ | _ | 6.56 | 3 phase 400V/50Hz 6 poli EC | 53 | _ | 218 | X | X |  |  |  | X |  | _
474 | X |  |  | 4266 | 2383 | 2500 | 1533 | glycol (34 %) - water | 80 | 5 | 428 | 10 | 30 | 126000 | _ |  | 6 | 800 | _ | _ | 9.84 | 3 phase 400V/50Hz 6 poli EC | 55 | _ | 236 | X | X |  |  |  | X |  | _
475 | X |  |  | 4266 | 2383 | 2500 | 1685 | glycol (34 %) - water | 87.2 | 5 | 466 | 10 | 56 | 120600 | _ |  | 6 | 800 | _ | _ | 9.84 | 3 phase 400V/50Hz 6 poli EC | 55 | _ | 290 | X | X |  |  |  | X |  | _
476 | X |  |  | 5688 | 2383 | 2500 | 1881 | glycol (34 %) - water | 108.4 | 5 | 580 | 10 | 63 | 168000 | _ |  | 8 | 800 | _ | _ | 13.12 | 3 phase 400V/50Hz 6 poli EC | 56 | _ | 288 | X | X |  |  |  | X |  | _
477 | X |  |  | 5688 | 2383 | 2500 | 2083 | glycol (34 %) - water | 115.8 | 5 | 619 | 10 | 51 | 160800 | _ |  | 8 | 800 | _ | _ | 13.12 | 3 phase 400V/50Hz 6 poli EC | 56 | _ | 362 | X | X |  |  |  | X |  | _
478 | X |  |  | 7110 | 2383 | 2500 | 2233 | glycol (34 %) - water | 136.7 | 5 | 731 | 10 | 94 | 210000 | _ |  | 10 | 800 | _ | _ | 16.4 | 3 phase 400V/50Hz 6 poli EC | 57 | _ | 342 | X | X |  |  |  | X |  | _
479 | X |  |  | 2844 | 2383 | 2500 | 1064 | glycol (34 %) - water | 49.1 | 5 | 263 | 10 | 54 | 73200 | _ |  | 4 | 900 | _ | _ | 4.08 | 3 phase 400V/50Hz 8 poli EC | 50 | _ | 182 | X | X |  |  |  | X |  | _
480 | X |  |  | 2844 | 2383 | 2500 | 1166 | glycol (34 %) - water | 51.2 | 5 | 274 | 10 | 40 | 69200 | _ |  | 4 | 900 | _ | _ | 4.08 | 3 phase 400V/50Hz 8 poli EC | 50 | _ | 218 | X | X |  |  |  | X |  | _
481 | X |  |  | 4266 | 2383 | 2500 | 1533 | glycol (34 %) - water | 74.7 | 5 | 399 | 10 | 65 | 109800 | _ |  | 6 | 900 | _ | _ | 6.12 | 3 phase 400V/50Hz 8 poli EC | 52 | _ | 236 | X | X |  |  |  | X |  | _
482 | X |  |  | 4266 | 2383 | 2500 | 1685 | glycol (34 %) - water | 77.8 | 5 | 416 | 10 | 45 | 103800 | _ |  | 6 | 900 | _ | _ | 6.12 | 3 phase 400V/50Hz 8 poli EC | 52 | _ | 290 | X | X |  |  |  | X |  | _
483 | X |  |  | 5688 | 2383 | 2500 | 1881 | glycol (34 %) - water | 99.1 | 5 | 530 | 10 | 53 | 146400 | _ |  | 8 | 900 | _ | _ | 8.16 | 3 phase 400V/50Hz 8 poli EC | 52 | _ | 288 | X | X |  |  |  | X |  | _
484 | X |  |  | 5688 | 2383 | 2500 | 2083 | glycol (34 %) - water | 103.4 | 5 | 553 | 10 | 41 | 138400 | _ |  | 8 | 900 | _ | _ | 8.16 | 3 phase 400V/50Hz 8 poli EC | 53 | _ | 362 | X | X |  |  |  | X |  | _
485 | X |  |  | 7110 | 2383 | 2500 | 2233 | glycol (34 %) - water | 125 | 5 | 668 | 10 | 80 | 183000 | _ |  | 10 | 900 | _ | _ | 10.2 | 3 phase 400V/50Hz 8 poli EC | 53 | _ | 342 | X | X |  |  |  | X |  | _
486 | X |  |  | 2844 | 2383 | 2500 | 1064 | glycol (34 %) - water | 42.7 | 5 | 229 | 10 | 42 | 61600 | _ |  | 4 | 800 | _ | _ | 3.2 | 3 phase 400V/50Hz 8 poli EC | 54 | _ | 182 | X | X |  |  |  | X |  | _
487 | X |  |  | 2844 | 2383 | 2500 | 1166 | glycol (34 %) - water | 44.4 | 5 | 237 | 10 | 31 | 59200 | _ |  | 4 | 800 | _ | _ | 3.2 | 3 phase 400V/50Hz 8 poli EC | 46 | _ | 218 | X | X |  |  |  | X |  | _
488 | X |  |  | 4266 | 2383 | 2500 | 1533 | glycol (34 %) - water | 65.1 | 5 | 348 | 10 | 51 | 92400 | _ |  | 6 | 800 | _ | _ | 4.8 | 3 phase 400V/50Hz 8 poli EC | 48 | _ | 236 | X | X |  |  |  | X |  | _
489 | X |  |  | 4266 | 2383 | 2500 | 1685 | glycol (34 %) - water | 67.4 | 5 | 361 | 10 | 35 | 88800 | _ |  | 6 | 800 | _ | _ | 4.8 | 3 phase 400V/50Hz 8 poli EC | 48 | _ | 290 | X | X |  |  |  | X |  | _
490 | X |  |  | 5688 | 2383 | 2500 | 1881 | glycol (34 %) - water | 86.3 | 5 | 462 | 10 | 41 | 123200 | _ |  | 8 | 800 | _ | _ | 6.4 | 3 phase 400V/50Hz 8 poli EC | 49 | _ | 288 | X | X |  |  |  | X |  | _
491 | X |  |  | 5688 | 2383 | 2500 | 2083 | glycol (34 %) - water | 89.5 | 5 | 479 | 10 | 31 | 118400 | _ |  | 8 | 800 | _ | _ | 6.4 | 3 phase 400V/50Hz 8 poli EC | 49 | _ | 362 | X | X |  |  |  | X |  | _
492 | X |  |  | 7110 | 2383 | 2500 | 2233 | glycol (34 %) - water | 108.9 | 5 | 582 | 10 | 62 | 154000 | _ |  | 10 | 800 | _ | _ | 8 | 3 phase 400V/50Hz 8 poli EC | 50 | _ | 342 | X | X |  |  |  | X |  | _
493 | X |  |  | 847 | 440 | 763 | 57 | Water | 1.797 | 5 | 10 | 5 | 16.2 | _ | _ | _ | 1 | _ | _ | _ | 0.5 | 3 phase 230 ± 10% V/50 | 48 | _ | _ | X |  |  |  |  | X |  | _
494 | X |  |  | 1682 | 440 | 763 | 109 | Water | 3.47 | 5 | 20 | 5 | 26.7 | _ | _ | _ | 2 | _ | _ | _ | 1 | 3 phase 230 ± 10% V/50 or 3 phase 400V/50 Hz | 51 | _ | _ | X |  |  |  |  | X |  | _
495 | X |  |  | 2145 | 779 | 1364 | 413 | Water | 5.315 | 5 | 31 | 5 | 33.7 | _ | _ | _ | 1 | _ | _ | _ | 2 | 3 phase 400V/50Hz | 60 | _ | _ | X |  |  |  |  | X |  | _
496 | X |  |  | 2145 | 779 | 1364 | 423 | Water | 7.052 | 5 | 41 | 5 | 36.7 | _ | _ | _ | 1 | _ | _ | _ | 2 | 3 phase 400V/50Hz | 59 | _ | _ | X |  |  |  |  | X |  | _
497 | X |  |  | 2145 | 779 | 1364 | 433 | Water | 8.522 | 5 | 49 | 5 | 38.4 | _ | _ | _ | 1 | _ | _ | _ | 2 | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  |  | X |  | _
498 | X |  |  | 3042 | 779 | 1364 | 562 | Water | 11.899 | 5 | 69 | 5 | 60 | _ | _ | _ | 2 | _ | _ | _ | 4 | 3 phase 400V/50Hz | 62 | _ | _ | X |  |  |  |  | X
499 | X |  |  | 3959 | 779 | 1364 | 679 | Water | 16.821 | 5 | 97 | 5 | 34.1 | _ | _ | _ | 2 | _ | _ | _ | 4 | 3 phase 400V/50Hz | 61 | _ | _ | X |  |  |  |  | X
500 | X |  |  | 4860 | 779 | 1364 | 821 | Water | 23.126 | 5 | 133 | 5 | 63.9 | _ | _ | _ | 3 | _ | _ | _ | 6 | 3 phase 400V/50Hz | 63 | _ | _ | X |  |  |  |  | X
501 | X |  |  | 4390 | 1510 | 1485 | 1064 | Water | 33.822 | 5 | 195 | 5 | 33 | _ | _ | _ | 4 | _ | _ | _ | 8 | 3 phase 400V/50Hz | 64 | _ | _ | X |  |  |  |  | X
502 | X |  |  | 5295 | 1510 | 1485 | 1271 | Water | 43.079 | 5 | 248 | 5 | 53 | _ | _ | _ | 5 | _ | _ | _ | 10 | 3 phase 400V/50Hz | 65 | _ | _ | X |  |  |  |  | X
503 | X |  |  | 5295 | 1510 | 2085 | 1543 | Water | 52.783 | 5 | 304 | 5 | 39 | _ | _ | _ | 5 | _ | _ | _ | 10 | 3 phase 400V/50Hz | 64 | _ | _ | X |  |  |  |  | X
504 | X |  |  | 6200 | 1510 | 2085 | 1803 | Water | 64.653 | 5 | 372 | 5 | 66 | _ | _ | _ | 6 | _ | _ | _ | 12 | 3 phase 400V/50Hz | 66 | _ | _ | X |  |  |  |  | X
505 | X |  |  | _ | _ | _ | 570 - 630 | Water | _ | 5 | 100 - 168 | 10 | _ | _ | _ | 2 | 12 | 800 | _ | _ | _ | 3 phase 400V/50Hz or 1 phase | 76 ÷ 90 | _ | 50 ÷ 67 | X |  |  |  |  | X |  | _
506 | X |  |  | 760 | 620 | 820 | _ | glycol (34 %) - water | 0.864 | 5 | 4.6 | 10 | _ | 2500 | _ | 2 | 1 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 36 | _ | _ | X |  |  |  | X |  |  | _
507 | X |  |  | 760 | 620 | 820 | _ | glycol (34 %) - water | 1.3899 | 5 | 7.4 | 10 | _ | 2400 | _ | 4 | 1 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 36 | _ | _ | X |  |  |  | X |  |  | _
508 | X |  |  | 1310 | 620 | 820 | _ | glycol (34 %) - water | 1.728 | 5 | 9.2 | 10 | _ | 5000 | _ | 3 | 2 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 39 | _ | _ | X |  |  |  | X |  |  | _
509 | X |  |  | 1860 | 620 | 820 | _ | glycol (34 %) - water | 2.6296 | 5 | 14 | 10 | _ | 7500 | _ | 2 | 3 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 41 | _ | _ | X |  |  |  | X |  |  | _
510 | X |  |  | 1310 | 1200 | 820 | _ | glycol (34 %) - water | 3.3809 | 5 | 18 | 10 | _ | 10000 | _ | 2 | 4 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 42 | _ | _ | X |  |  |  | X |  |  | _
511 | X |  |  | 1860 | 1200 | 820 | _ | glycol (34 %) - water | 5.2591 | 5 | 28 | 10 | _ | 15000 | _ | 2 | 6 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 44 | _ | _ | X |  |  |  | X |  |  | _
512 | X |  |  | 760 | 620 | 820 | _ | glycol (34 %) - water | 0.67617 | 5 | 3.6 | 10 | _ | 1500 | _ | 2 | 1 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 26 | _ | _ | X |  |  |  | X |  |  | _
513 | X |  |  | 1310 | 620 | 820 | _ | glycol (34 %) - water | 1.3899 | 5 | 7.4 | 10 | _ | 3000 | _ | 3 | 2 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 29 | _ | _ | X |  |  |  | X |  |  | _
514 | X |  |  | 1860 | 620 | 820 | _ | glycol (34 %) - water | 2.0661 | 5 | 11 | 10 | _ | 4500 | _ | 2 | 3 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 31 | _ | _ | X |  |  |  | X |  |  | _
515 | X |  |  | 1310 | 1200 | 820 | _ | glycol (34 %) - water | 2.8174 | 5 | 15 | 10 | _ | 6000 | _ | 2 | 4 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 32 | _ | _ | X |  |  |  | X |  |  | _
516 | X |  |  | 1860 | 1200 | 820 | _ | glycol (34 %) - water | 4.5078 | 5 | 24 | 10 | _ | 9000 | _ | 2 | 6 | 300 | _ | _ | _ | 3 phase 400V/50Hz | 34 | _ | _ | X |  |  |  | X |  |  | _
517 | X |  |  | 1105 | 833 | 1060 | _ | glycol (34 %) - water | 3.193 | 5 | 17 | 10 | _ | 7750 | _ | 3 | 1 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 48 | _ | _ | X |  |  |  | X |  |  | _
518 | X |  |  | 1105 | 833 | 1060 | _ | glycol (34 %) - water | 4.32 | 5 | 23 | 10 | _ | 7100 | _ | 5 | 1 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 48 | _ | _ | X |  |  |  | X |  |  | _
519 | X |  |  | 2045 | 833 | 1060 | _ | glycol (34 %) - water | 4.8835 | 5 | 26 | 10 | _ | 16000 | _ | 2 | 2 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  | X |  |  | _
520 | X |  |  | 2045 | 833 | 1060 | _ | glycol (34 %) - water | 7.8887 | 5 | 42 | 10 | _ | 14800 | _ | 4 | 2 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  | X |  |  | _
521 | X |  |  | 2985 | 833 | 1060 | _ | glycol (34 %) - water | 10.1426 | 5 | 54 | 10 | _ | 23250 | _ | 3 | 3 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  | X |  |  | _
522 | X |  |  | 3925 | 833 | 1060 | _ | glycol (34 %) - water | 13.3356 | 5 | 71 | 10 | _ | 31000 | _ | 3 | 4 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
523 | X |  |  | 2985 | 833 | 1060 | _ | glycol (34 %) - water | 20.2852 | 5 | 108 | 10 | _ | 46500 | _ | 3 | 6 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  | X |  |  | _
524 | X |  |  | 3925 | 833 | 1060 | _ | glycol (34 %) - water | 26.6713 | 5 | 142 | 10 | _ | 62000 | _ | 3 | 8 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 57 | _ | _ | X |  |  |  | X |  |  | _
525 | X |  |  | 1105 | 833 | 1060 | _ | glycol (34 %) - water | 3.0052 | 5 | 16 | 10 | _ | 7360 | _ | 3 | 1 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 45 | _ | _ | X |  |  |  | X |  |  | _
526 | X |  |  | 2045 | 833 | 1060 | _ | glycol (34 %) - water | 4.8835 | 5 | 26 | 10 | _ | 15200 | _ | 5 | 5 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 48 | _ | _ | X |  |  |  | X |  |  | _
527 | X |  |  | 2045 | 833 | 1060 | _ | glycol (34 %) - water | 7.7009 | 5 | 41 | 10 | _ | 14060 | _ | 4 | 2 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 48 | _ | _ | X |  |  |  | X |  |  | _
528 | X |  |  | 2985 | 833 | 1060 | _ | glycol (34 %) - water | 9.7669 | 5 | 52 | 10 | _ | 22080 | _ | 3 | 3 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  | X |  |  | _
529 | X |  |  | 3925 | 833 | 1060 | _ | glycol (34 %) - water | 12.96 | 5 | 69 | 10 | _ | 29440 | _ | 3 | 4 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  | X |  |  | _
530 | X |  |  | 2985 | 833 | 1060 | _ | glycol (34 %) - water | 19.5339 | 5 | 104 | 10 | _ | 44160 | _ | 3 | 6 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  | X |  |  | _
531 | X |  |  | 3925 | 833 | 1060 | _ | glycol (34 %) - water | 25.7321 | 5 | 137 | 10 | _ | 58880 | _ | 3 | 8 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
532 | X |  |  | 3925 | 833 | 1060 | _ | glycol (34 %) - water | 34.7478 | 5 | 185 | 10 | _ | 53960 | _ | 5 | 8 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
533 | X |  |  | 1340 | 1033 | 1200 | _ | glycol (34 %) - water | 4.32 | 5 | 23 | 10 | _ | 9550 | _ | 3 | 1 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  | X |  |  | _
534 | X |  |  | 2500 | 1033 | 1200 | _ | glycol (34 %) - water | 9.0156 | 5 | 48 | 10 | _ | 19100 | _ | 3 | 2 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  | X |  |  | _
535 | X |  |  | 3660 | 1033 | 1200 | _ | glycol (34 %) - water | 13.8991 | 5 | 74 | 10 | _ | 28650 | _ | 3 | 3 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
536 | X |  |  | 4820 | 1033 | 1200 | _ | glycol (34 %) - water | 18.4069 | 5 | 98 | 10 | _ | 38200 | _ | 3 | 4 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  | X |  |  | _
537 | X |  |  | 3660 | 1033 | 1200 | _ | glycol (34 %) - water | 27.6104 | 5 | 147 | 10 | _ | 57300 | _ | 3 | 6 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 57 | _ | _ | X |  |  |  | X |  |  | _
538 | X |  |  | 4820 | 1033 | 1200 | _ | glycol (34 %) - water | 36.626 | 5 | 195 | 10 | _ | 76400 | _ | 3 | 8 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  | X |  |  | _
539 | X |  |  | 4820 | 1033 | 1200 | _ | glycol (34 %) - water | 46.2052 | 5 | 246 | 10 | _ | 69600 | _ | 5 | 8 | 600 | _ | _ | _ | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  | X |  |  | _
540 | X |  |  | 1633 | 1434 | 1530 | _ | glycol (34 %) - water | 8.8278 | 5 | 47 | 10 | _ | 20400 | _ | 3 | 1 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  | X |  |  | _
541 | X |  |  | 3063 | 1434 | 1530 | _ | glycol (34 %) - water | 18.0313 | 5 | 96 | 10 | _ | 40800 | _ | 3 | 2 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 59 | _ | _ | X |  |  |  | X |  |  | _
542 | X |  |  | 4493 | 1434 | 1530 | _ | glycol (34 %) - water | 27.0469 | 5 | 144 | 10 | _ | 61200 | _ | 3 | 3 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 61 | _ | _ | X |  |  |  | X |  |  | _
543 | X |  |  | 3063 | 1434 | 1530 | _ | glycol (34 %) - water | 35.8747 | 5 | 191 | 10 | _ | 81600 | _ | 3 | 4 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 62 | _ | _ | X |  |  |  | X |  |  | _
544 | X |  |  | 4493 | 1434 | 1530 | _ | glycol (34 %) - water | 54.2817 | 5 | 289 | 10 | _ | 122400 | _ | 3 | 6 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 64 | _ | _ | X |  |  |  | X |  |  | _
545 | X |  |  | 4493 | 1434 | 1530 | _ | glycol (34 %) - water | 73.2521 | 5 | 390 | 10 | _ | 106200 | _ | 6 | 6 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 64 | _ | _ | X |  |  |  | X |  |  | _
546 | X |  |  | 1633 | 1434 | 1530 | _ | glycol (34 %) - water | 7.3252 | 5 | 39 | 10 | _ | 15000 | _ | 3 | 1 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  | X |  |  | _
547 | X |  |  | 3063 | 1434 | 1530 | _ | glycol (34 %) - water | 14.6504 | 5 | 78 | 10 | _ | 30000 | _ | 3 | 2 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  | X |  |  | _
548 | X |  |  | 4493 | 1434 | 1530 | _ | glycol (34 %) - water | 22.1634 | 5 | 118 | 10 | _ | 45000 | _ | 3 | 3 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  | X |  |  | _
549 | X |  |  | 4493 | 1434 | 1530 | _ | glycol (34 %) - water | 29.6765 | 5 | 158 | 10 | _ | 38700 | _ | 6 | 3 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  | X |  |  | _
550 | X |  |  | 3063 | 1434 | 1530 | _ | glycol (34 %) - water | 29.3008 | 5 | 156 | 10 | _ | 60000 | _ | 3 | 4 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  | X |  |  | _
551 | X |  |  | 4493 | 1434 | 1530 | _ | glycol (34 %) - water | 44.1391 | 5 | 235 | 10 | _ | 90000 | _ | 3 | 6 | 900 | _ | _ | _ | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  | X |  |  | _
552 | X |  |  | 1610 | 780 | 1065 | _ | glycol (34 %) - water | 8.64 | 5 | 46 | 10 | _ | 15800 | _ | 3 | 2 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  | X |  |  | _
553 | X |  |  | 2265 | 780 | 1065 | _ | glycol (34 %) - water | 12.96 | 5 | 69 | 10 | _ | 23700 | _ | 3 | 3 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  | X |  |  | _
554 | X |  |  | 2920 | 780 | 1065 | _ | glycol (34 %) - water | 17.28 | 5 | 92 | 10 | _ | 31600 | _ | 3 | 4 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
555 | X |  |  | 3575 | 780 | 1065 | _ | glycol (34 %) - water | 21.6 | 5 | 115 | 10 | _ | 39500 | _ | 3 | 5 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  | X |  |  | _
556 | X |  |  | 1610 | 780 | 1065 | _ | glycol (34 %) - water | 7.1374 | 5 | 38 | 10 | _ | 10400 | _ | 3 | 2 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 41 | _ | _ | X |  |  |  | X |  |  | _
557 | X |  |  | 2265 | 780 | 1065 | _ | glycol (34 %) - water | 10.7061 | 5 | 57 | 10 | _ | 15600 | _ | 3 | 3 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 43 | _ | _ | X |  |  |  | X |  |  | _
558 | X |  |  | 2920 | 780 | 1065 | _ | glycol (34 %) - water | 14.2748 | 5 | 76 | 10 | _ | 20800 | _ | 3 | 4 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 44 | _ | _ | X |  |  |  | X |  |  | _
559 | X |  |  | 3575 | 780 | 1065 | _ | glycol (34 %) - water | 17.8435 | 5 | 95 | 10 | _ | 26000 | _ | 3 | 5 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 45 | _ | _ | X |  |  |  | X |  |  | _
560 | X |  |  | 1610 | 780 | 1065 | _ | glycol (34 %) - water | 5.0713 | 5 | 27 | 10 | _ | 6800 | _ | 3 | 2 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  | X |  |  | _
561 | X |  |  | 2265 | 780 | 1065 | _ | glycol (34 %) - water | 7.7009 | 5 | 41 | 10 | _ | 10200 | _ | 3 | 3 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  | X |  |  | _
562 | X |  |  | 2920 | 780 | 1065 | _ | glycol (34 %) - water | 10.1426 | 5 | 54 | 10 | _ | 13600 | _ | 3 | 4 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
563 | X |  |  | 3575 | 780 | 1065 | _ | glycol (34 %) - water | 12.3965 | 5 | 66 | 10 | _ | 17000 | _ | 3 | 5 | 500 | _ | _ | _ | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  | X |  |  | _
564 | X |  |  | 2270 | 1100 | 1590 | _ | glycol (34 %) - water | 24.6052 | 5 | 131 | 10 | _ | 46000 | _ | 3 | 2 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 51 | _ | _ | X |  |  |  | X |  |  | _
565 | X |  |  | 3210 | 1100 | 1590 | _ | glycol (34 %) - water | 38.3165 | 5 | 204 | 10 | _ | 70000 | _ | 3 | 3 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  | X |  |  | _
566 | X |  |  | 4180 | 1100 | 1590 | _ | glycol (34 %) - water | 51.6521 | 5 | 275 | 10 | _ | 92000 | _ | 3 | 4 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
567 | X |  |  | 5150 | 1100 | 1590 | _ | glycol (34 %) - water | 63.4851 | 5 | 338 | 10 | _ | 114000 | _ | 3 | 5 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  | X |  |  | _
568 | X |  |  | 3250 | 2200 | 2090 | _ | glycol (34 %) - water | 51.6521 | 5 | 275 | 10 | _ | 84000 | _ | 3 | 4 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
569 | X |  |  | 3850 | 2200 | 2090 | _ | glycol (34 %) - water | 73.4399 | 5 | 391 | 10 | _ | 122000 | _ | 3 | 6 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  | X |  |  | _
570 | X |  |  | 5100 | 2200 | 2090 | _ | glycol (34 %) - water | 98.6086 | 5 | 525 | 10 | _ | 165000 | _ | 3 | 8 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 57 | _ | _ | X |  |  |  | X |  |  | _
571 | X |  |  | 8100 | 2200 | 2090 | _ | glycol (34 %) - water | 126.5946 | 5 | 674 | 10 | _ | 205000 | _ | 3 | 10 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  | X |  |  | _
572 | X |  |  | 8700 | 2200 | 2090 | _ | glycol (34 %) - water | 146.8798 | 5 | 782 | 10 | _ | 242000 | _ | 3 | 12 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 59 | _ | _ | X |  |  |  | X |  |  | _
573 | X |  |  | 9950 | 2200 | 2090 | _ | glycol (34 %) - water | 172.0485 | 5 | 916 | 10 | _ | 282000 | _ | 3 | 14 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 59 | _ | _ | X |  |  |  | X |  |  | _
574 | X |  |  | 11200 | 2200 | 2090 | _ | glycol (34 %) - water | 197.2171 | 5 | 1050 | 10 | _ | 324000 | _ | 3 | 16 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 60 | _ | _ | X |  |  |  | X |  |  | _
575 | X |  |  | 11200 | 2200 | 2090 | _ | glycol (34 %) - water | 213.7458 | 5 | 1138 | 10 | _ | 296000 | _ | 4 | 16 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 60 | _ | _ | X |  |  |  | X |  |  | _
576 | X |  |  | 2270 | 1850 | 2150 | _ | glycol (34 %) - water | 43.5756 | 5 | 232 | 10 | _ | 77100 | _ | 3 | 4 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 54 | _ | _ | X |  |  |  | X |  |  | _
577 | X |  |  | 3240 | 1850 | 2150 | _ | glycol (34 %) - water | 65.5512 | 5 | 349 | 10 | _ | 115700 | _ | 3 | 6 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  | X |  |  | _
578 | X |  |  | 4120 | 1850 | 2150 | _ | glycol (34 %) - water | 87.7147 | 5 | 467 | 10 | _ | 154200 | _ | 3 | 8 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 57 | _ | _ | X |  |  |  | X |  |  | _
579 | X |  |  | 5180 | 1850 | 2150 | _ | glycol (34 %) - water | 109.5025 | 5 | 583 | 10 | _ | 192800 | _ | 3 | 10 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  | X |  |  | _
580 | X |  |  | 2270 | 1850 | 2150 | _ | glycol (34 %) - water | 35.3113 | 5 | 188 | 10 | _ | 55000 | _ | 3 | 4 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 46 | _ | _ | X |  |  |  | X |  |  | _
581 | X |  |  | 3240 | 1850 | 2150 | _ | glycol (34 %) - water | 53.7182 | 5 | 286 | 10 | _ | 82000 | _ | 3 | 6 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 48 | _ | _ | X |  |  |  | X |  |  | _
582 | X |  |  | 4210 | 1850 | 2150 | _ | glycol (34 %) - water | 72.1251 | 5 | 384 | 10 | _ | 110000 | _ | 3 | 8 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  | X |  |  | _
583 | X |  |  | 5180 | 1850 | 2150 | _ | glycol (34 %) - water | 89.4051 | 5 | 476 | 10 | _ | 136000 | _ | 3 | 10 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  | X |  |  | _
584 | X |  |  | 2270 | 1850 | 2150 | _ | glycol (34 %) - water | 25.7321 | 5 | 137 | 10 | _ | 33350 | _ | 3 | 4 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 36 | _ | _ | X |  |  |  | X |  |  | _
585 | X |  |  | 3240 | 1850 | 2150 | _ | glycol (34 %) - water | 38.6921 | 5 | 206 | 10 | _ | 49900 | _ | 3 | 6 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 38 | _ | _ | X |  |  |  | X |  |  | _
586 | X |  |  | 4210 | 1850 | 2150 | _ | glycol (34 %) - water | 51.4643 | 5 | 274 | 10 | _ | 66600 | _ | 3 | 8 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 39 | _ | _ | X |  |  |  | X |  |  | _
587 | X |  |  | 5180 | 1850 | 2150 | _ | glycol (34 %) - water | 64.4243 | 5 | 343 | 10 | _ | 83250 | _ | 3 | 10 | 800 | _ | _ | _ | 3 phase 400V/50Hz | 40 | _ | _ | X |  |  |  | X |  |  | _
588 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 116.2 | _ | _ | 23876 |  |  | 2 | 500 | _ | 451 | 2.2 | 3 phase 400V/50Hz or 1 phase | 48 | 348 | 40.1 | X |  |  |  |  | X
589 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 109.73 | _ | _ | 21564 |  |  | 2 | 500 |  | 473 | 2.2 | 3 phase 400V/50Hz or 1 phase | 48 | 348 | 40.1 | X |  |  |  |  | X
590 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 103.91 | _ | _ | 20460 |  |  | 2 | 500 |  | 527 | 2.2 | 3 phase 400V/50Hz or 1 phase | 50 | 348 | 40.1 | X |  |  |  |  | X
591 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 96.27 | _ | _ | 18988 |  |  | 2 | 500 |  | 575 | 2.2 | 3 phase 400V/50Hz or 1 phase | 51 | 348 | 40.1 | X |  |  |  |  | X
592 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 88.37 | _ | _ | 16488 |  |  | 2 | 500 |  | 591 | 2.2 | 3 phase 400V/50Hz or 1 phase | 53 | 348 | 40.1 | X |  |  |  |  | X
593 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 137.83 | _ | _ | 29392 |  |  | 2 | 500 |  | 545 | 4.4 | 3 phase 400V/50Hz or 1 phase | 51 | 348 | 40.1 | X |  |  |  |  | X
594 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 132.89 | _ | _ | 28200 |  |  | 2 | 500 |  | 568 | 4.4 | 3 phase 400V/50Hz or 1 phase | 53 | 348 | 40.1 | X |  |  |  |  | X
595 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 128.49 | _ | _ | 25584 |  |  | 2 | 500 |  | 580 | 4.4 | 3 phase 400V/50Hz or 1 phase | 53 | 348 | 40.1 | X |  |  |  |  | X
596 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 123.84 | _ | _ | 25640 |  |  | 2 | 500 |  | 614 | 4.4 | 3 phase 400V/50Hz or 1 phase | 53 | 348 | 40.1 | X |  |  |  |  | X
597 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 119.05 | _ | _ | 22948 |  |  | 2 | 500 |  | 634 | 4.4 | 3 phase 400V/50Hz or 1 phase | 56 | 348 | 40.1 | X |  |  |  |  | X
598 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 158.64 | _ | _ | 35638 |  |  | 2 | 500 |  | 638 | 8 | 3 phase 400V/50Hz or 1 phase | 56 | 348 | 40.1 | X |  |  |  |  | X
599 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 155.53 | _ | _ | 34624 |  |  | 2 | 500 |  | 667 | 8 | 3 phase 400V/50Hz or 1 phase | 57 | 348 | 40.1 | X |  |  |  |  | X
600 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 152.29 | _ | _ | 35380 |  |  | 2 | 500 |  | 720 | 8 | 3 phase 400V/50Hz or 1 phase | 56 | 348 | 40.1 | X |  |  |  |  | X
601 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 163.04 | _ | _ | 36652 |  |  | 2 | 500 |  | 760 | 11 | 3 phase 400V/50Hz or 1 phase | 61 | 348 | 40.1 | X |  |  |  |  | X
602 | X |  |  | 2020 | 1350 | 1770 | 525 | Water | _ | _ | 159.93 | _ | _ | 36657 |  |  | 2 | 500 |  | 805 | 11 | 3 phase 400V/50Hz or 1 phase | 61 | 348 | 40.1 | X |  |  |  |  | X
603 | X |  |  | 2440 | 2080 | 1820 | 653 | Water | 18.2077 | 5 | 105 | 10 | _ | 43520 |  |  | 3 | 630 |  | 1380 | 4.95 | 3 phase 400V/50Hz | 57 | 190 | 21.8 | X |  |  |  |  | X
604 | X |  |  | 2440 | 2080 | 1820 | 685 | Water | 23.2365 | 5 | 134 | 10 | _ | 41890 |  |  | 3 | 630 |  | 1380 | 4.95 | 3 phase 400V/50Hz | 57 | 285 | 32.7 | X |  |  |  |  | X
605 | X |  |  | 2440 | 2080 | 1820 | 720 | Water | 26.1844 | 5 | 151 | 10 | _ | 39950 |  |  | 3 | 630 |  | 1380 | 4.95 | 3 phase 400V/50Hz | 57 | 387 | 44.2 | X |  |  |  |  | X
606 | X |  |  | 3230 | 2080 | 1820 | 818 | Water | 31.0398 | 5 | 179 | 10 | _ | 55860 |  |  | 4 | 630 |  | 1380 | 6.6 | 3 phase 400V/50Hz | 58 | 387 | 44.2 | X |  |  |  |  | X
607 | X |  |  | 3230 | 2080 | 1820 | 860 | Water | 35.0282 | 5 | 202 | 10 | _ | 53270 |  |  | 4 | 630 |  | 1380 | 6.6 | 3 phase 400V/50Hz | 58 | 517 | 59 | X |  |  |  |  | X
608 | X |  |  | 4010 | 2080 | 1820 | 993 | Water | 39.0165 | 5 | 225 | 10 | _ | 69830 |  |  | 5 | 630 |  | 1380 | 8.25 | 3 phase 400V/50Hz | 59 | 490 | 55.7 | X |  |  |  |  | X
609 | X |  |  | 4010 | 2080 | 1820 | 1032 | Water | 43.8719 | 5 | 253 | 10 | _ | 66590 |  |  | 5 | 630 |  | 1380 | 8.25 | 3 phase 400V/50Hz | 59 | 654 | 74.4 | X |  |  |  |  | X
610 | X |  |  | 2440 | 2080 | 1820 | 653 | Water | 13.491 | 5 | 77.8 | 10 | _ | 24890 |  |  | 3 | 630 |  | 890 | 1.8 | 3 phase 400V/50Hz | 48 | 190 | 21.8 | X |  |  |  |  | X
611 | X |  |  | 2440 | 2080 | 1820 | 685 | Water | 16.1268 | 5 | 93 | 10 | _ | 23680 |  |  | 3 | 630 |  | 890 | 1.8 | 3 phase 400V/50Hz | 48 | 285 | 32.7 | X |  |  |  |  | X
612 | X |  |  | 2440 | 2080 | 1820 | 720 | Water | 17.254 | 5 | 99.5 | 10 | _ | 22470 |  |  | 3 | 630 |  | 890 | 1.8 | 3 phase 400V/50Hz | 48 | 387 | 44.2 | X |  |  |  |  | X
613 | X |  |  | 3230 | 2080 | 1820 | 818 | Water | 21.5024 | 5 | 124 | 10 | _ | 31570 |  |  | 4 | 630 |  | 890 | 2.4 | 3 phase 400V/50Hz | 49 | 387 | 44.2 | X |  |  |  |  | X
614 | X |  |  | 3230 | 2080 | 1820 | 860 | Water | 23.0631 | 5 | 133 | 10 | _ | 29970 |  |  | 4 | 630 |  | 890 | 2.4 | 3 phase 400V/50Hz | 49 | 517 | 59 | X |  |  |  |  | X
615 | X |  |  | 4010 | 2080 | 1820 | 993 | Water | 27.0515 | 5 | 156 | 10 | _ | 39470 |  |  | 5 | 630 |  | 890 | 3 | 3 phase 400V/50Hz | 50 | 490 | 55.7 | X |  |  |  |  | X
616 | X |  |  | 4010 | 2080 | 1820 | 1032 | Water | 28.9589 | 5 | 167 | 10 | _ | 37460 |  |  | 5 | 630 |  | 890 | 3 | 3 phase 400V/50Hz | 50 | 654 | 74.4 | X |  |  |  |  | X
617 | X |  |  | 2440 | 2080 | 1820 | 653 | Water | 11.2714 | 5 | 65 | 10 | _ | 18550 |  |  | 3 | 630 |  | 660 | 0.99 | 3 phase 400V/50Hz | 38 | 190 | 21.8 | X |  |  |  |  | X
618 | X |  |  | 2440 | 2080 | 1820 | 685 | Water | 12.7107 | 5 | 73.3 | 10 | _ | 17100 |  |  | 3 | 630 |  | 660 | 0.99 | 3 phase 400V/50Hz | 38 | 285 | 32.7 | X |  |  |  |  | X
619 | X |  |  | 2440 | 2080 | 1820 | 818 | Water | 16.9939 | 5 | 98 | 10 | _ | 22800 |  |  | 4 | 630 |  | 660 | 1.32 | 3 phase 400V/50Hz | 39 | 387 | 44.2 | X |  |  |  |  | X
620 | X |  |  | 3230 | 2080 | 1820 | 860 | Water | 17.6875 | 5 | 102 | 10 | _ | 21580 |  |  | 4 | 630 |  | 660 | 1.32 | 3 phase 400V/50Hz | 39 | 517 | 59 | X |  |  |  |  | X
621 | X |  |  | 4010 | 2080 | 1820 | 993 | Water | 21.329 | 5 | 123 | 10 | _ | 28490 |  |  | 5 | 630 |  | 660 | 1.65 | 3 phase 400V/50Hz | 40 | 490 | 55.7 | X |  |  |  |  | X
622 | X |  |  | 4010 | 2080 | 1820 | 1032 | Water | 22.0227 | 5 | 127 | 10 | _ | 26980 |  |  | 5 | 630 |  | 660 | 1.65 | 3 phase 400V/50Hz | 40 | 654 | 74.4 | X |  |  |  |  | X
623 | X |  |  | 2440 | 2080 | 1820 | 653 | Water | 8.1328 | 5 | 46.9 | 10 | _ | 11510 |  |  | 3 | 630 |  | 450 | 0.435 | 3 phase 400V/50Hz | 28 | 190 | 21.8 | X |  |  |  |  | X
624 | X |  |  | 2440 | 2080 | 1820 | 685 | Water | 8.7744 | 5 | 50.6 | 10 | _ | 10800 |  |  | 3 | 630 |  | 450 | 0.435 | 3 phase 400V/50Hz | 28 | 285 | 32.7 | X |  |  |  |  | X
625 | X |  |  | 3230 | 2080 | 1820 | 818 | Water | 11.7223 | 5 | 67.6 | 10 | _ | 14390 |  |  | 4 | 630 |  | 450 | 0.58 | 3 phase 400V/50Hz | 29 | 387 | 44.2 | X |  |  |  |  | X
626 | X |  |  | 4010 | 2080 | 1820 | 993 | Water | 14.6702 | 5 | 84.6 | 10 | _ | 17990 |  |  | 5 | 630 |  | 450 | 0.725 | 3 phase 400V/50Hz | 30 | 490 | 55.7 | X |  |  |  |  | X
627 | X |  |  | 1240 | 767 | 954 | 63 | Water | 3.8843 | 5 | 22.4 | 10 | _ | 7230 |  |  | 1 | 500 | 1180 | 1390 | 0.72 | 3 phase 400V/50Hz | 50 | 25 | 3.7 | X |  |  |  |  | X |  |  |  | X
628 | X |  |  | 1240 | 767 | 954 | 68 | Water | 4.5606 | 5 | 26.3 | 10 | _ | 6690 |  |  | 1 | 500 | 1180 | 1390 | 0.72 | 3 phase 400V/50Hz | 50 | 37 | 5.5 | X |  |  |  |  | X |  |  |  | X
629 | X |  |  | 1240 | 767 | 954 | 73 | Water | 4.8901 | 5 | 28.2 | 10 | _ | 6280 |  |  | 1 | 500 | 1180 | 1390 | 0.72 | 3 phase 400V/50Hz | 50 | 50 | 7.3 | X |  |  |  |  | X |  |  |  | X
630 | X |  |  | 2120 | 767 | 954 | 103 | Water | 7.7686 | 5 | 44.8 | 10 | _ | 14460 |  |  | 2 | 500 | 1180 | 1390 | 1.44 | 3 phase 400V/50Hz | 53 | 50 | 7.4 | X |  |  |  |  | X |  |  |  | X
631 | X |  |  | 2120 | 767 | 954 | 111 | Water | 9.1212 | 5 | 52.6 | 10 | _ | 13380 |  |  | 2 | 500 | 1180 | 1390 | 1.44 | 3 phase 400V/50Hz | 53 | 74 | 11 | X |  |  |  |  | X |  |  |  | X
632 | X |  |  | 2120 | 767 | 954 | 121 | Water | 9.7801 | 5 | 56.4 | 10 | _ | 12560 |  |  | 2 | 500 | 1180 | 1390 | 1.44 | 3 phase 400V/50Hz | 53 | 99 | 14.6 | X |  |  |  |  | X |  |  |  | X
633 | X |  |  | 3000 | 767 | 954 | 141 | Water | 11.6529 | 5 | 67.2 | 10 | _ | 21690 |  |  | 3 | 500 | 1180 | 1390 | 2.16 | 3 phase 400V/50Hz | 54 | 74 | 11.1 | X |  |  |  |  | X |  |  |  | X
634 | X |  |  | 3000 | 767 | 954 | 155 | Water | 13.6818 | 5 | 78.9 | 10 | _ | 20070 |  |  | 3 | 500 | 1180 | 1390 | 2.16 | 3 phase 400V/50Hz | 54 | 111 | 16.5 | X |  |  |  |  | X |  |  |  | X
635 | X |  |  | 3000 | 767 | 954 | 168 | Water | 14.6702 | 5 | 84.6 | 10 | _ | 18840 |  |  | 3 | 500 | 1180 | 1390 | 2.16 | 3 phase 400V/50Hz | 54 | 149 | 21.9 | X |  |  |  |  | X |  |  |  | X
636 | X |  |  | 2120 | 1517 | 954 | 187 | Water | 15.5372 | 5 | 89.6 | 10 | _ | 28920 |  |  | 4 | 500 | 1180 | 1390 | 2.88 | 3 phase 400V/50Hz | 56 | 99 | 14.8 | X |  |  |  |  | X |  |  |  | X
637 | X |  |  | 2120 | 1517 | 954 | 208 | Water | 18.2077 | 5 | 105 | 10 | _ | 26760 |  |  | 4 | 500 | 1180 | 1390 | 2.88 | 3 phase 400V/50Hz | 56 | 149 | 22 | X |  |  |  |  | X |  |  |  | X
638 | X |  |  | 2120 | 1517 | 954 | 227 | Water | 19.595 | 5 | 113 | 10 | _ | 25120 |  |  | 4 | 500 | 1180 | 1390 | 2.88 | 3 phase 400V/50Hz | 56 | 198 | 29.2 | X |  |  |  |  | X |  |  |  | X
639 | X |  |  | 3000 | 1517 | 954 | 265 | Water | 23.2365 | 5 | 134 | 10 | _ | 43380 |  |  | 6 | 500 | 1180 | 1390 | 4.32 | 3 phase 400V/50Hz | 57 | 149 | 22.2 | X |  |  |  |  | X |  |  |  | X
640 | X |  |  | 3000 | 1517 | 954 | 293 | Water | 27.3983 | 5 | 158 | 10 | _ | 40140 |  |  | 6 | 500 | 1180 | 1390 | 4.32 | 3 phase 400V/50Hz | 57 | 223 | 33 | X |  |  |  |  | X |  |  |  | X
641 | X |  |  | 3000 | 1517 | 954 | 320 | Water | 29.3057 | 5 | 169 | 10 | _ | 37680 |  |  | 6 | 500 | 1180 | 1390 | 4.32 | 3 phase 400V/50Hz | 57 | 297 | 43.8 | X |  |  |  |  | X |  |  |  | X
642 | X |  |  | 1240 | 767 | 954 | 61 | Water | 3.104 | 5 | 17.9 | 10 | _ | 4970 |  |  | 1 | 500 | 800 | 930 | 0.27 | 3 phase 400V/50Hz | 37 | 25 | 3.7 | X |  |  |  |  | X |  |  |  | X
643 | X |  |  | 1240 | 767 | 954 | 66 | Water | 3.4508 | 5 | 19.9 | 10 | _ | 4500 |  |  | 1 | 500 | 800 | 930 | 0.27 | 3 phase 400V/50Hz | 37 | 37 | 5.5 | X |  |  |  |  | X |  |  |  | X
644 | X |  |  | 1240 | 767 | 954 | 71 | Water | 3.5028 | 5 | 20.2 | 10 | _ | 4180 |  |  | 1 | 500 | 800 | 930 | 0.27 | 3 phase 400V/50Hz | 37 | 50 | 7.3 | X |  |  |  |  | X |  |  |  | X
645 | X |  |  | 2120 | 767 | 954 | 98 | Water | 6.208 | 5 | 35.8 | 10 | _ | 9940 |  |  | 2 | 500 | 800 | 930 | 0.54 | 3 phase 400V/50Hz | 40 | 50 | 7.4 | X |  |  |  |  | X |  |  |  | X
646 | X |  |  | 2120 | 767 | 954 | 107 | Water | 6.9016 | 5 | 39.8 | 10 | _ | 9000 |  |  | 2 | 500 | 800 | 930 | 0.54 | 3 phase 400V/50Hz | 40 | 74 | 11 | X |  |  |  |  | X |  |  |  | X
647 | X |  |  | 2120 | 767 | 954 | 117 | Water | 7.0056 | 5 | 40.4 | 10 | _ | 8360 |  |  | 2 | 500 | 800 | 930 | 0.54 | 3 phase 400V/50Hz | 40 | 99 | 14.6 | X |  |  |  |  | X |  |  |  | X
648 | X |  |  | 3000 | 767 | 954 | 135 | Water | 9.3119 | 5 | 53.7 | 10 | _ | 14910 |  |  | 3 | 500 | 800 | 930 | 0.81 | 3 phase 400V/50Hz | 42 | 74 | 11.1 | X |  |  |  |  | X |  |  |  | X
649 | X |  |  | 3000 | 767 | 954 | 149 | Water | 10.3524 | 5 | 59.7 | 10 | _ | 13500 |  |  | 3 | 500 | 800 | 930 | 0.81 | 3 phase 400V/50Hz | 42 | 111 | 16.5 | X |  |  |  |  | X |  |  |  | X
650 | X |  |  | 3000 | 767 | 954 | 162 | Water | 10.5085 | 5 | 60.6 | 10 | _ | 12540 |  |  | 3 | 500 | 800 | 930 | 0.81 | 3 phase 400V/50Hz | 42 | 149 | 21.9 | X |  |  |  |  | X |  |  |  | X
651 | X |  |  | 2120 | 1517 | 954 | 178 | Water | 12.4159 | 5 | 71.6 | 10 | _ | 19880 |  |  | 4 | 500 | 800 | 930 | 1.08 | 3 phase 400V/50Hz | 43 | 99 | 14.8 | X |  |  |  |  | X |  |  |  | X
652 | X |  |  | 2120 | 1517 | 954 | 200 | Water | 13.8032 | 5 | 79.6 | 10 | _ | 18000 |  |  | 4 | 500 | 800 | 930 | 1.08 | 3 phase 400V/50Hz | 43 | 149 | 22 | X |  |  |  |  | X |  |  |  | X
653 | X |  |  | 2120 | 1517 | 954 | 218 | Water | 14.0113 | 5 | 80.8 | 10 | _ | 16720 |  |  | 4 | 500 | 800 | 930 | 1.08 | 3 phase 400V/50Hz | 43 | 198 | 29.2 | X |  |  |  |  | X |  |  |  | X
654 | X |  |  | 3000 | 1517 | 954 | 253 | Water | 18.5545 | 5 | 107 | 10 | _ | 29820 |  |  | 6 | 500 | 800 | 930 | 1.62 | 3 phase 400V/50Hz | 45 | 149 | 22.2 | X |  |  |  |  | X |  |  |  | X
655 | X |  |  | 3000 | 1517 | 954 | 280 | Water | 20.6354 | 5 | 119 | 10 | _ | 27000 |  |  | 6 | 500 | 800 | 930 | 1.62 | 3 phase 400V/50Hz | 45 | 223 | 33 | X |  |  |  |  | X |  |  |  | X
656 | X |  |  | 3000 | 1517 | 954 | 308 | Water | 20.9822 | 5 | 121 | 10 | _ | 25080 |  |  | 6 | 500 | 800 | 930 | 1.62 | 3 phase 400V/50Hz | 45 | 297 | 43.8 | X |  |  |  |  | X |  |  |  | X
657 | X |  |  | 1240 | 767 | 954 | 61 | Water | 2.445 | 5 | 14.1 | 10 | _ | 3430 |  |  | 1 | 500 | 560 | 680 | 0.15 | 3 phase 400V/50Hz | 29 | 25 | 3.7 | X |  |  |  |  | X |  |  |  | X
658 | X |  |  | 1240 | 767 | 954 | 66 | Water | 2.5664 | 5 | 14.8 | 10 | _ | 3100 |  |  | 1 | 500 | 560 | 680 | 0.15 | 3 phase 400V/50Hz | 29 | 37 | 5.5 | X |  |  |  |  | X |  |  |  | X
659 | X |  |  | 1240 | 767 | 954 | 71 | Water | 2.6358 | 5 | 15.2 | 10 | _ | 3170 |  |  | 1 | 500 | 560 | 680 | 0.15 | 3 phase 400V/50Hz | 29 | 50 | 7.3 | X |  |  |  |  | X |  |  |  | X
660 | X |  |  | 2120 | 767 | 954 | 98 | Water | 4.8901 | 5 | 28.2 | 10 | _ | 6860 |  |  | 2 | 500 | 560 | 680 | 0.3 | 3 phase 400V/50Hz | 32 | 50 | 7.4 | X |  |  |  |  | X |  |  |  | X
661 | X |  |  | 2120 | 767 | 954 | 107 | Water | 5.1328 | 5 | 29.6 | 10 | _ | 6200 |  |  | 2 | 500 | 560 | 680 | 0.3 | 3 phase 400V/50Hz | 32 | 74 | 11 | X |  |  |  |  | X |  |  |  | X
662 | X |  |  | 2120 | 767 | 954 | 117 | Water | 5.2716 | 5 | 30.4 | 10 | _ | 6340 |  |  | 2 | 500 | 560 | 680 | 0.3 | 3 phase 400V/50Hz | 32 | 99 | 14.6 | X |  |  |  |  | X |  |  |  | X
663 | X |  |  | 3000 | 767 | 954 | 135 | Water | 7.3351 | 5 | 42.3 | 10 | _ | 10290 |  |  | 3 | 500 | 560 | 680 | 0.45 | 3 phase 400V/50Hz | 33 | 74 | 11.1 | X |  |  |  |  | X |  |  |  | X
664 | X |  |  | 3000 | 767 | 954 | 149 | Water | 7.6993 | 5 | 44.4 | 10 | _ | 9300 |  |  | 3 | 500 | 560 | 680 | 0.45 | 3 phase 400V/50Hz | 33 | 111 | 16.5 | X |  |  |  |  | X |  |  |  | X
665 | X |  |  | 3000 | 767 | 954 | 162 | Water | 7.9073 | 5 | 45.6 | 10 | _ | 9510 |  |  | 3 | 500 | 560 | 680 | 0.45 | 3 phase 400V/50Hz | 33 | 149 | 21.9 | X |  |  |  |  | X |  |  |  | X
666 | X |  |  | 2120 | 1517 | 954 | 178 | Water | 9.7801 | 5 | 56.4 | 10 | _ | 13720 |  |  | 4 | 500 | 560 | 680 | 0.6 | 3 phase 400V/50Hz | 34 | 99 | 14.8 | X |  |  |  |  | X |  |  |  | X
667 | X |  |  | 2120 | 1517 | 954 | 200 | Water | 10.2657 | 5 | 59.2 | 10 | _ | 12400 |  |  | 4 | 500 | 560 | 680 | 0.6 | 3 phase 400V/50Hz | 34 | 149 | 22 | X |  |  |  |  | X |  |  |  | X
668 | X |  |  | 2120 | 1517 | 954 | 218 | Water | 10.5431 | 5 | 60.8 | 10 | _ | 12680 |  |  | 4 | 500 | 560 | 680 | 0.6 | 3 phase 400V/50Hz | 34 | 198 | 29.2 | X |  |  |  |  | X |  |  |  | X
669 | X |  |  | 3000 | 1517 | 954 | 253 | Water | 14.6702 | 5 | 84.6 | 10 | _ | 20580 |  |  | 6 | 500 | 560 | 680 | 0.9 | 3 phase 400V/50Hz | 36 | 149 | 22.2 | X |  |  |  |  | X |  |  |  | X
670 | X |  |  | 3000 | 1517 | 954 | 280 | Water | 15.3985 | 5 | 88.8 | 10 | _ | 18600 |  |  | 6 | 500 | 560 | 680 | 0.9 | 3 phase 400V/50Hz | 36 | 223 | 33 | X |  |  |  |  | X |  |  |  | X
671 | X |  |  | 3000 | 1517 | 954 | 308 | Water | 15.8147 | 5 | 91.2 | 10 | _ | 19020 |  |  | 6 | 500 | 560 | 680 | 0.9 | 3 phase 400V/50Hz | 36 | 297 | 43.8 | X |  |  |  |  | X |  |  |  | X
672 | X |  |  | 1240 | 767 | 954 | 58 | Water | 1.9595 | 5 | 11.3 | 10 | _ | 2540 |  |  | 1 | 500 | 340 | 560 | 0.1 | 3 phase 400V/50Hz | 27 | 25 | 3.7 | X |  |  |  |  | X |  |  |  | X
673 | X |  |  | 1240 | 767 | 954 | 63 | Water | 1.9422 | 5 | 11.2 | 10 | _ | 2260 |  |  | 1 | 500 | 340 | 560 | 0.1 | 3 phase 400V/50Hz | 27 | 37 | 5.5 | X |  |  |  |  | X |  |  |  | X
674 | X |  |  | 1240 | 767 | 954 | 68 | Water | 1.9422 | 5 | 11.2 | 10 | _ | 2260 |  |  | 1 | 500 | 340 | 560 | 0.1 | 3 phase 400V/50Hz | 27 | 50 | 7.3 | X |  |  |  |  | X |  |  |  | X
675 | X |  |  | 2120 | 767 | 954 | 92 | Water | 3.9017 | 5 | 22.5 | 10 | _ | 5080 |  |  | 2 | 500 | 340 | 560 | 0.2 | 3 phase 400V/50Hz | 30 | 50 | 7.4 | X |  |  |  |  | X |  |  |  | X
676 | X |  |  | 2120 | 767 | 954 | 102 | Water | 3.8843 | 5 | 22.4 | 10 | _ | 4520 |  |  | 2 | 500 | 340 | 560 | 0.2 | 3 phase 400V/50Hz | 30 | 74 | 11 | X |  |  |  |  | X |  |  |  | X
677 | X |  |  | 2120 | 767 | 954 | 111 | Water | 3.8843 | 5 | 22.4 | 10 | _ | 4520 |  |  | 2 | 500 | 340 | 560 | 0.2 | 3 phase 400V/50Hz | 30 | 99 | 14.6 | X |  |  |  |  | X |  |  |  | X
678 | X |  |  | 3000 | 767 | 954 | 126 | Water | 5.8611 | 5 | 33.8 | 10 | _ | 7620 |  |  | 3 | 500 | 340 | 560 | 0.3 | 3 phase 400V/50Hz | 31 | 74 | 11.1 | X |  |  |  |  | X |  |  |  | X
679 | X |  |  | 3000 | 767 | 954 | 139 | Water | 5.8265 | 5 | 33.6 | 10 | _ | 6780 |  |  | 3 | 500 | 340 | 560 | 0.3 | 3 phase 400V/50Hz | 31 | 111 | 16.5 | X |  |  |  |  | X |  |  |  | X
680 | X |  |  | 3000 | 767 | 954 | 154 | Water | 5.8265 | 5 | 33.6 | 10 | _ | 6780 |  |  | 3 | 500 | 340 | 560 | 0.3 | 3 phase 400V/50Hz | 31 | 149 | 21.9 | X |  |  |  |  | X |  |  |  | X
681 | X |  |  | 2120 | 1517 | 954 | 167 | Water | 7.8033 | 5 | 45 | 10 | _ | 10160 |  |  | 4 | 500 | 340 | 560 | 0.4 | 3 phase 400V/50Hz | 32 | 99 | 14.8 | X |  |  |  |  | X |  |  |  | X
682 | X |  |  | 2120 | 1517 | 954 | 188 | Water | 7.7686 | 5 | 44.8 | 10 | _ | 9040 |  |  | 4 | 500 | 340 | 560 | 0.4 | 3 phase 400V/50Hz | 32 | 149 | 22 | X |  |  |  |  | X |  |  |  | X
683 | X |  |  | 2120 | 1517 | 954 | 207 | Water | 7.7686 | 5 | 44.8 | 10 | _ | 9040 |  |  | 4 | 500 | 340 | 560 | 0.4 | 3 phase 400V/50Hz | 32 | 198 | 29.2 | X |  |  |  |  | X |  |  |  | X
684 | X |  |  | 3000 | 1517 | 954 | 235 | Water | 11.7223 | 5 | 67.6 | 10 | _ | 15240 |  |  | 6 | 500 | 340 | 560 | 0.6 | 3 phase 400V/50Hz | 34 | 149 | 22.2 | X |  |  |  |  | X |  |  |  | X
685 | X |  |  | 3000 | 1517 | 954 | 262 | Water | 11.6356 | 5 | 67.1 | 10 | _ | 13560 |  |  | 6 | 500 | 340 | 560 | 0.6 | 3 phase 400V/50Hz | 34 | 223 | 33 | X |  |  |  |  | X |  |  |  | X
686 | X |  |  | 3000 | 1517 | 954 | 290 | Water | 11.6529 | 5 | 67.2 | 10 | _ | 13560 |  |  | 6 | 500 | 340 | 560 | 0.6 | 3 phase 400V/50Hz | 34 | 297 | 43.8 | X |  |  |  |  | X |  |  |  | X
687 | X |  |  | 1360 | 1067 | 1080 | 109 | Water | 7.3524 | 5 | 42.4 | 10 | _ | 14400 |  |  | 1 | 630 | 1140 | 1380 | 1.65 | 3 phase 400V/50Hz | 53 | 39 | 5.8 | X |  |  |  |  | X |  |  |  | X
688 | X |  |  | 1360 | 1067 | 1080 | 117 | Water | 8.8611 | 5 | 51.1 | 10 | _ | 13510 |  |  | 1 | 630 | 1140 | 1380 | 1.65 | 3 phase 400V/50Hz | 53 | 59 | 8.7 | X |  |  |  |  | X |  |  |  | X
689 | X |  |  | 1360 | 1067 | 1080 | 125 | Water | 9.52 | 5 | 54.9 | 10 | _ | 12620 |  |  | 1 | 630 | 1140 | 1380 | 1.65 | 3 phase 400V/50Hz | 53 | 79 | 11.6 | X |  |  |  |  | X |  |  |  | X
690 | X |  |  | 2360 | 1067 | 1080 | 184 | Water | 14.7049 | 5 | 84.8 | 10 | _ | 28800 |  |  | 2 | 630 | 1140 | 1380 | 3.3 | 3 phase 400V/50Hz | 56 | 79 | 11.6 | X |  |  |  |  | X |  |  |  | X
691 | X |  |  | 2360 | 1067 | 1080 | 199 | Water | 17.6875 | 5 | 102 | 10 | _ | 27020 |  |  | 2 | 630 | 1140 | 1380 | 3.3 | 3 phase 400V/50Hz | 56 | 118 | 17.4 | X |  |  |  |  | X |  |  |  | X
692 | X |  |  | 2360 | 1067 | 1080 | 214 | Water | 19.0747 | 5 | 110 | 10 | _ | 25240 |  |  | 2 | 630 | 1140 | 1380 | 3.3 | 3 phase 400V/50Hz | 56 | 158 | 23.2 | X |  |  |  |  | X |  |  |  | X
693 | X |  |  | 3360 | 1067 | 1080 | 261 | Water | 22.0227 | 5 | 127 | 10 | _ | 43200 |  |  | 3 | 630 | 1140 | 1380 | 4.95 | 3 phase 400V/50Hz | 57 | 118 | 17.4 | X |  |  |  |  | X |  |  |  | X
694 | X |  |  | 3360 | 1067 | 1080 | 283 | Water | 26.5312 | 5 | 153 | 10 | _ | 40530 |  |  | 3 | 630 | 1140 | 1380 | 4.95 | 3 phase 400V/50Hz | 57 | 177 | 26.1 | X |  |  |  |  | X |  |  |  | X
695 | X |  |  | 3360 | 1067 | 1080 | 305 | Water | 28.6121 | 5 | 165 | 10 | _ | 37860 |  |  | 3 | 630 | 1140 | 1380 | 4.95 | 3 phase 400V/50Hz | 57 | 236 | 34.8 | X |  |  |  |  | X |  |  |  | X
696 | X |  |  | 1360 | 1067 | 1080 | 109 | Water | 5.2369 | 5 | 30.2 | 10 | _ | 8140 |  |  | 1 | 630 | 690 | 890 | 0.6 | 3 phase 400V/50Hz | 43 | 39 | 5.8 | X |  |  |  |  | X |  |  |  | X
697 | X |  |  | 1360 | 1067 | 1080 | 117 | Water | 5.7398 | 5 | 33.1 | 10 | _ | 7590 |  |  | 1 | 630 | 690 | 890 | 0.6 | 3 phase 400V/50Hz | 43 | 59 | 8.7 | X |  |  |  |  | X |  |  |  | X
698 | X |  |  | 1360 | 1067 | 1080 | 125 | Water | 5.9132 | 5 | 34.1 | 10 | _ | 7170 |  |  | 1 | 630 | 690 | 890 | 0.6 | 3 phase 400V/50Hz | 43 | 79 | 11.6 | X |  |  |  |  | X |  |  |  | X
699 | X |  |  | 2360 | 1067 | 1080 | 184 | Water | 10.4738 | 5 | 60.4 | 10 | _ | 16280 |  |  | 2 | 630 | 690 | 890 | 1.2 | 3 phase 400V/50Hz | 46 | 79 | 11.6 | X |  |  |  |  | X |  |  |  | X
700 | X |  |  | 2360 | 1067 | 1080 | 199 | Water | 11.4795 | 5 | 66.2 | 10 | _ | 15180 |  |  | 2 | 630 | 690 | 890 | 1.2 | 3 phase 400V/50Hz | 46 | 118 | 17.4 | X |  |  |  |  | X |  |  |  | X
701 | X |  |  | 2360 | 1067 | 1080 | 214 | Water | 11.8263 | 5 | 68.2 | 10 | _ | 14340 |  |  | 2 | 630 | 690 | 890 | 1.2 | 3 phase 400V/50Hz | 46 | 158 | 23.2 | X |  |  |  |  | X |  |  |  | X
702 | X |  |  | 3360 | 1067 | 1080 | 261 | Water | 15.7107 | 5 | 90.6 | 10 | _ | 24420 |  |  | 3 | 630 | 690 | 890 | 1.8 | 3 phase 400V/50Hz | 48 | 118 | 17.4 | X |  |  |  |  | X |  |  |  | X
703 | X |  |  | 3360 | 1067 | 1080 | 283 | Water | 17.2193 | 5 | 99.3 | 10 | _ | 22770 |  |  | 3 | 630 | 690 | 890 | 1.8 | 3 phase 400V/50Hz | 48 | 177 | 26.1 | X |  |  |  |  | X |  |  |  | X
704 | X |  |  | 3360 | 1067 | 1080 | 305 | Water | 17.6875 | 5 | 102 | 10 | _ | 21510 |  |  | 3 | 630 | 690 | 890 | 1.8 | 3 phase 400V/50Hz | 48 | 236 | 34.8 | X |  |  |  |  | X |  |  |  | X
705 | X |  |  | 1660 | 1067 | 1150 | 111 | Water | 6.7282 | 5 | 38.8 | 10 | _ | 10550 |  |  | 1 | 710 | 670 | 880 | 0.84 | 3 phase 400V/50Hz | 46 | 51 | 7.5 | X |  |  |  |  | X |  |  |  | X
706 | X |  |  | 1660 | 1067 | 1150 | 122 | Water | 7.5952 | 5 | 43.8 | 10 | _ | 9900 |  |  | 1 | 710 | 670 | 880 | 0.84 | 3 phase 400V/50Hz | 46 | 77 | 11.2 | X |  |  |  |  | X |  |  |  | X
707 | X |  |  | 1660 | 1067 | 1150 | 131 | Water | 7.8553 | 5 | 45.3 | 10 | _ | 9900 |  |  | 1 | 710 | 670 | 880 | 0.84 | 3 phase 400V/50Hz | 46 | 102 | 15 | X |  |  |  |  | X |  |  |  | X
708 | X |  |  | 2960 | 1067 | 1150 | 178 | Water | 13.4564 | 5 | 77.6 | 10 | _ | 21100 |  |  | 2 | 710 | 670 | 880 | 1.68 | 3 phase 400V/50Hz | 48 | 102 | 14.7 | X |  |  |  |  | X |  |  |  | X
709 | X |  |  | 2960 | 1067 | 1150 | 198 | Water | 15.1904 | 5 | 87.6 | 10 | _ | 19800 |  |  | 2 | 710 | 670 | 880 | 1.68 | 3 phase 400V/50Hz | 48 | 154 | 22.1 | X |  |  |  |  | X |  |  |  | X
710 | X |  |  | 2960 | 1067 | 1150 | 216 | Water | 15.7107 | 5 | 90.6 | 10 | _ | 19800 |  |  | 2 | 710 | 670 | 880 | 1.68 | 3 phase 400V/50Hz | 48 | 205 | 29.5 | X |  |  |  |  | X |  |  |  | X
711 | X |  |  | 4260 | 1067 | 1150 | 247 | Water | 20.1152 | 5 | 116 | 10 | _ | 31650 |  |  | 3 | 710 | 670 | 880 | 2.52 | 3 phase 400V/50Hz | 50 | 154 | 22 | X |  |  |  |  | X |  |  |  | X
712 | X |  |  | 4260 | 1067 | 1150 | 276 | Water | 22.7163 | 5 | 131 | 10 | _ | 29700 |  |  | 3 | 710 | 670 | 880 | 2.52 | 3 phase 400V/50Hz | 50 | 230 | 33 | X |  |  |  |  | X |  |  |  | X
713 | X |  |  | 4260 | 1067 | 1150 | 304 | Water | 23.5833 | 5 | 136 | 10 | _ | 29700 |  |  | 3 | 710 | 670 | 880 | 2.52 | 3 phase 400V/50Hz | 50 | 307 | 44 | X |  |  |  |  | X |  |  |  | X
714 | X |  |  | 5560 | 1067 | 1150 | 316 | Water | 26.8781 | 5 | 155 | 10 | _ | 42200 |  |  | 4 | 710 | 670 | 880 | 3.36 | 3 phase 400V/50Hz | 51 | 205 | 29.2 | X |  |  |  |  | X |  |  |  | X
715 | X |  |  | 5560 | 1067 | 1150 | 358 | Water | 30.3462 | 5 | 175 | 10 | _ | 39600 |  |  | 4 | 710 | 670 | 880 | 3.36 | 3 phase 400V/50Hz | 51 | 307 | 43.9 | X |  |  |  |  | X |  |  |  | X
716 | X |  |  | 5560 | 1067 | 1150 | 391 | Water | 31.3866 | 5 | 181 | 10 | _ | 39600 |  |  | 4 | 710 | 670 | 880 | 3.36 | 3 phase 400V/50Hz | 51 | 410 | 58.5 | X |  |  |  |  | X |  |  |  | X
717 | X |  |  | 1660 | 1067 | 1150 | 111 | Water | 5.4623 | 5 | 31.5 | 10 | _ | 7650 |  |  | 1 | 710 | 475 | 645 | 0.44 | 3 phase 400V/50Hz | 37 | 51 | 7.5 | X |  |  |  |  | X |  |  |  | X
718 | X |  |  | 1660 | 1067 | 1150 | 122 | Water | 5.8785 | 5 | 33.9 | 10 | _ | 7140 |  |  | 1 | 710 | 475 | 645 | 0.44 | 3 phase 400V/50Hz | 37 | 77 | 11.2 | X |  |  |  |  | X |  |  |  | X
719 | X |  |  | 1660 | 1067 | 1150 | 131 | Water | 5.9825 | 5 | 34.5 | 10 | _ | 7140 |  |  | 1 | 710 | 475 | 645 | 0.44 | 3 phase 400V/50Hz | 37 | 102 | 15 | X |  |  |  |  | X |  |  |  | X
720 | X |  |  | 2960 | 1067 | 1150 | 178 | Water | 10.9246 | 5 | 63 | 10 | _ | 15300 |  |  | 2 | 710 | 475 | 645 | 0.88 | 3 phase 400V/50Hz | 40 | 102 | 14.7 | X |  |  |  |  | X |  |  |  | X
721 | X |  |  | 2960 | 1067 | 1150 | 198 | Water | 11.757 | 5 | 67.8 | 10 | _ | 14280 |  |  | 2 | 710 | 475 | 645 | 0.88 | 3 phase 400V/50Hz | 40 | 154 | 22.1 | X |  |  |  |  | X |  |  |  | X
722 | X |  |  | 2960 | 1067 | 1150 | 216 | Water | 11.9651 | 5 | 69 | 10 | _ | 14280 |  |  | 2 | 710 | 475 | 645 | 0.88 | 3 phase 400V/50Hz | 40 | 205 | 29.5 | X |  |  |  |  | X |  |  |  | X
723 | X |  |  | 4260 | 1067 | 1150 | 247 | Water | 16.3869 | 5 | 94.5 | 10 | _ | 22950 |  |  | 3 | 710 | 475 | 645 | 1.32 | 3 phase 400V/50Hz | 42 | 154 | 22 | X |  |  |  |  | X |  |  |  | X
724 | X |  |  | 4260 | 1067 | 1150 | 276 | Water | 17.6875 | 5 | 102 | 10 | _ | 21420 |  |  | 3 | 710 | 475 | 645 | 1.32 | 3 phase 400V/50Hz | 42 | 230 | 33 | X |  |  |  |  | X |  |  |  | X
725 | X |  |  | 4260 | 1067 | 1150 | 304 | Water | 17.8609 | 5 | 103 | 10 | _ | 21420 |  |  | 3 | 710 | 475 | 645 | 1.32 | 3 phase 400V/50Hz | 42 | 307 | 44 | X |  |  |  |  | X |  |  |  | X
726 | X |  |  | 5560 | 1067 | 1150 | 316 | Water | 21.8493 | 5 | 126 | 10 | _ | 30600 |  |  | 4 | 710 | 475 | 645 | 1.76 | 3 phase 400V/50Hz | 43 | 205 | 29.2 | X |  |  |  |  | X |  |  |  | X
727 | X |  |  | 5560 | 1067 | 1150 | 358 | Water | 23.5833 | 5 | 136 | 10 | _ | 28560 |  |  | 4 | 710 | 475 | 645 | 1.76 | 3 phase 400V/50Hz | 43 | 307 | 43.9 | X |  |  |  |  | X |  |  |  | X
728 | X |  |  | 5560 | 1067 | 1150 | 391 | Water | 23.9301 | 5 | 138 | 10 | _ | 28560 |  |  | 4 | 710 | 475 | 645 | 1.76 | 3 phase 400V/50Hz | 43 | 410 | 58.5 | X |  |  |  |  | X |  |  |  | X
729 | X |  |  | 1865 | 1245 | 1386 | 192 | Water | 9.6241 | 5 | 55.5 | 10 | _ | 20160 |  |  | 1 | 800 | 685 | 895 | 2 | 3 phase 400V/50Hz | 49 | 101 | 12 | X |  |  |  |  | X |  |  |  | X
730 | X |  |  | 1865 | 1245 | 1386 | 222 | Water | 12.0171 | 5 | 69.3 | 10 | _ | 19500 |  |  | 1 | 800 | 685 | 895 | 2 | 3 phase 400V/50Hz | 49 | 151 | 18 | X |  |  |  |  | X |  |  |  | X
731 | X |  |  | 1865 | 1245 | 1386 | 232 | Water | 13.3176 | 5 | 76.8 | 10 | _ | 18660 |  |  | 1 | 800 | 685 | 895 | 2 | 3 phase 400V/50Hz | 49 | 201 | 23 | X |  |  |  |  | X |  |  |  | X
732 | X |  |  | 1865 | 1245 | 1386 | 242 | Water | 14.0286 | 5 | 80.9 | 10 | _ | 17980 |  |  | 1 | 800 | 685 | 895 | 2 | 3 phase 400V/50Hz | 49 | 251 | 28.75 | X |  |  |  |  | X |  |  |  | X
733 | X |  |  | 3340 | 1245 | 1386 | 304 | Water | 19.2482 | 5 | 111 | 10 | _ | 40320 |  |  | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 201 | 24 | X |  |  |  |  | X |  |  |  | X
734 | X |  |  | 3340 | 1245 | 1386 | 358 | Water | 24.1035 | 5 | 139 | 10 | _ | 39000 |  |  | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 302 | 36 | X |  |  |  |  | X |  |  |  | X
735 | X |  |  | 3340 | 1245 | 1386 | 376 | Water | 26.7046 | 5 | 154 | 10 | _ | 37320 |  |  | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 402 | 46 | X |  |  |  |  | X |  |  |  | X
736 | X |  |  | 3340 | 1245 | 1386 | 394 | Water | 28.0919 | 5 | 162 | 10 | _ | 35960 |  |  | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 503 | 57.5 | X |  |  |  |  | X |  |  |  | X
737 | X |  |  | 3340 | 1245 | 1386 | 408 | Water | 24.4504 | 5 | 141 | 10 | _ | 44700 |  |  | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 302 | 36 | X |  |  |  |  | X |  |  |  | X
738 | X |  |  | 3340 | 1245 | 1386 | 490 | Water | 29.4792 | 5 | 170 | 10 | _ | 43110 |  |  | 2 | 800 | 685 | 895 | 4 | 3 phase 400V/50Hz | 51 | 453 | 54 | X |  |  |  |  | X |  |  |  | X
739 | X |  |  | 2355 | 1620 | 1697 | 330 | Water | 15.4332 | 5 | 89 | 10 | _ | 30020 |  |  | 1 | 1000 | 530 | 670 | 2.2 | 3 phase 400V/50Hz | 53 | 176 | 20 | X |  |  |  |  | X |  |  |  | X
740 | X |  |  | 2790 | 1620 | 1697 | 350 | Water | 17.1326 | 5 | 98.8 | 10 | _ | 30840 |  |  | 1 | 1000 | 530 | 670 | 2.2 | 3 phase 400V/50Hz | 53 | 215 | 25 | X |  |  |  |  | X |  |  |  | X
741 | X |  |  | 2355 | 1620 | 1697 | 340 | Water | 18.9013 | 5 | 109 | 10 | _ | 28960 |  |  | 1 | 1000 | 530 | 670 | 2.2 | 3 phase 400V/50Hz | 53 | 264 | 30 | X |  |  |  |  | X |  |  |  | X
742 | X |  |  | 2790 | 1620 | 1697 | 380 | Water | 20.8088 | 5 | 120 | 10 | _ | 30260 |  |  | 1 | 1000 | 530 | 670 | 2.2 | 3 phase 400V/50Hz | 53 | 322 | 37 | X |  |  |  |  | X |  |  |  | X
743 | X |  |  | 4320 | 1620 | 1697 | 551 | Water | 30.8664 | 5 | 178 | 10 | _ | 60040 |  |  | 2 | 1000 | 530 | 670 | 4.4 | 3 phase 400V/50Hz | 56 | 352 | 40 | X |  |  |  |  | X |  |  |  | X
744 | X |  |  | 5190 | 1620 | 1697 | 587 | Water | 34.3345 | 5 | 198 | 10 | _ | 61680 |  |  | 2 | 1000 | 530 | 670 | 4.4 | 3 phase 400V/50Hz | 56 | 430 | 50 | X |  |  |  |  | X |  |  |  | X
745 | X |  |  | 4320 | 1620 | 1697 | 569 | Water | 37.8027 | 5 | 218 | 10 | _ | 57920 |  |  | 2 | 1000 | 530 | 670 | 4.4 | 3 phase 400V/50Hz | 56 | 528 | 60 | X |  |  |  |  | X |  |  |  | X
746 | X |  |  | 5190 | 1620 | 1697 | 641 | Water | 41.6176 | 5 | 240 | 10 | _ | 60520 |  |  | 2 | 1000 | 530 | 670 | 4.4 | 3 phase 400V/50Hz | 56 | 644 | 74 | X |  |  |  |  | X |  |  |  | X
747 | X |  |  | 6285 | 1620 | 1697 | 814 | Water | 46.2996 | 5 | 267 | 10 | _ | 90060 |  |  | 3 | 1000 | 530 | 670 | 6.6 | 3 phase 400V/50Hz | 57 | 528 | 60 | X |  |  |  |  | X |  |  |  | X
748 | X |  |  | 5190 | 1620 | 1697 | 824 | Water | 51.3284 | 5 | 296 | 10 | _ | 92520 |  |  | 3 | 1000 | 530 | 670 | 6.6 | 3 phase 400V/50Hz | 57 | 644 | 75 | X |  |  |  |  | X |  |  |  | X
749 | X |  |  | 6285 | 1620 | 1697 | 842 | Water | 56.704 | 5 | 327 | 10 | _ | 86880 |  |  | 3 | 1000 | 530 | 670 | 6.6 | 3 phase 400V/50Hz | 57 | 791 | 90 | X |  |  |  |  | X |  |  |  | X
750 | X |  |  | 7590 | 1620 | 1697 | 902 | Water | 62.4264 | 5 | 360 | 10 | _ | 90780 |  |  | 3 | 1000 | 530 | 670 | 6.6 | 3 phase 400V/50Hz | 57 | 967 | 111 | X |  |  |  |  | X |  |  |  | X
751 | X |  |  | 8250 | 1620 | 1697 | 993 | Water | 61.7328 | 5 | 356 | 10 | _ | 120080 |  |  | 4 | 1000 | 530 | 670 | 8.8 | 3 phase 400V/50Hz | 58 | 704 | 80 | X |  |  |  |  | X |  |  |  | X
752 | X |  |  | 9990 | 1620 | 1697 | 1061 | Water | 68.4957 | 5 | 395 | 10 | _ | 123360 |  |  | 4 | 1000 | 530 | 670 | 8.8 | 3 phase 400V/50Hz | 58 | 859 | 100 | X |  |  |  |  | X |  |  |  | X
753 | X |  |  | 8250 | 1620 | 1697 | 1027 | Water | 75.6054 | 5 | 436 | 10 | _ | 115840 |  |  | 4 | 1000 | 530 | 670 | 8.8 | 3 phase 400V/50Hz | 58 | 1055 | 120 | X |  |  |  |  | X |  |  |  | X
754 | X |  |  | 9990 | 1620 | 1697 | 1163 | Water | 83.2353 | 5 | 480 | 10 | _ | 121040 |  |  | 4 | 1000 | 530 | 670 | 8.8 | 3 phase 400V/50Hz | 58 | 1289 | 148 | X |  |  |  |  | X |  |  |  | X
755 | X |  |  | 2520 | 2350 | 2450 | 1040 | Water | 44.739 | 5 | 258 | 10 | _ | 88100 |  |  | 4 | 800 | 685 | 895 | 8 | 3 phase 400V/50Hz | 54 | 506 | 74 | X |  |  |  |  | X
756 | X |  |  | 2520 | 2350 | 2450 | 1170 | Water | 54.1029 | 5 | 312 | 10 | _ | 82200 |  |  | 4 | 800 | 685 | 895 | 8 | 3 phase 400V/50Hz | 54 | 760 | 102 | X |  |  |  |  | X
757 | X |  |  | 2520 | 2350 | 2450 | 1300 | Water | 58.6115 | 5 | 338 | 10 | _ | 78400 |  |  | 4 | 800 | 685 | 895 | 8 | 3 phase 400V/50Hz | 54 | 1013 | 132 | X |  |  |  |  | X
758 | X |  |  | 3620 | 2350 | 2450 | 1470 | Water | 66.935 | 5 | 386 | 10 | _ | 132200 |  |  | 6 | 800 | 685 | 895 | 12 | 3 phase 400V/50Hz | 56 | 759 | 110 | X |  |  |  |  | X
759 | X |  |  | 3620 | 2350 | 2450 | 1660 | Water | 80.981 | 5 | 467 | 10 | _ | 123300 |  |  | 6 | 800 | 685 | 895 | 12 | 3 phase 400V/50Hz | 56 | 1139 | 154 | X |  |  |  |  | X
760 | X |  |  | 3620 | 2350 | 2450 | 1850 | Water | 87.9172 | 5 | 507 | 10 | _ | 117600 |  |  | 6 | 800 | 685 | 895 | 12 | 3 phase 400V/50Hz | 56 | 1519 | 198 | X |  |  |  |  | X
761 | X |  |  | 4720 | 2350 | 2450 | 1910 | Water | 89.8247 | 5 | 518 | 10 | _ | 176300 |  |  | 8 | 800 | 685 | 895 | 16 | 3 phase 400V/50Hz | 57 | 1012 | 148 | X |  |  |  |  | X
762 | X |  |  | 4720 | 2350 | 2450 | 2140 | Water | 108.0324 | 5 | 623 | 10 | _ | 164400 |  |  | 8 | 800 | 685 | 895 | 16 | 3 phase 400V/50Hz | 57 | 1519 | 198 | X |  |  |  |  | X
763 | X |  |  | 4720 | 2350 | 2450 | 2370 | Water | 117.223 | 5 | 676 | 10 | _ | 156800 |  |  | 8 | 800 | 685 | 895 | 16 | 3 phase 400V/50Hz | 57 | 2026 | 254 | X |  |  |  |  | X
764 | X |  |  | 5820 | 2350 | 2450 | 2330 | Water | 111.674 | 5 | 644 | 10 | _ | 220300 |  |  | 10 | 800 | 685 | 895 | 20 | 3 phase 400V/50Hz | 58 | 1265 | 186 | X |  |  |  |  | X
765 | X |  |  | 5820 | 2350 | 2450 | 2610 | Water | 135.0839 | 5 | 779 | 10 | _ | 205500 |  |  | 10 | 800 | 685 | 895 | 20 | 3 phase 400V/50Hz | 58 | 1899 | 264 | X |  |  |  |  | X
766 | X |  |  | 2270 | 2160 | 2150 | 740 | glycol (34 %) - water | 44 | 5 | 232 | 10 | 53 | 77100 |  | 2 | 4 | 800 | _ | 910 | 7.2 | 3 phase 400V/50Hz 6P | 54 | 484 | 84 | X |  |  |  |  | X
767 | X |  |  | 2270 | 2160 | 2150 | 800 | glycol (34 %) - water | 48 | 5 | 254 | 10 | 58 | 70400 |  | 2 | 4 | 800 | _ | 910 | 7.2 | 3 phase 400V/50Hz 6P | 54 | 646 | 112 | X |  |  |  |  | X
768 | X |  |  | 3240 | 2160 | 2150 | 1110 | glycol (34 %) - water | 65 | 5 | 349 | 10 | 57 | 115700 |  | 2 | 6 | 800 | _ | 910 | 10.8 | 3 phase 400V/50Hz 6P | 56 | 726 | 124 | X |  |  |  |  | X
769 | X |  |  | 3240 | 2160 | 2150 | 1200 | glycol (34 %) - water | 71 | 5 | 381 | 10 | 55 | 105500 |  | 2 | 6 | 800 | _ | 910 | 10.8 | 3 phase 400V/50Hz 6P | 56 | 970 | 166 | X |  |  |  |  | X
770 | X |  |  | 4210 | 2160 | 2150 | 1430 | glycol (34 %) - water | 88 | 5 | 467 | 10 | 54 | 154200 |  | 2 | 8 | 800 | _ | 910 | 14.4 | 3 phase 400V/50Hz 6P | 57 | 970 | 166 | X |  |  |  |  | X
771 | X |  |  | 4210 | 2160 | 2150 | 1550 | glycol (34 %) - water | 95 | 5 | 508 | 10 | 58 | 140700 |  | 2 | 8 | 800 | _ | 910 | 14.4 | 3 phase 400V/50Hz 6P | 57 | 1292 | 220 | X |  |  |  |  | X
772 | X |  |  | 5180 | 2160 | 2150 | 1850 | glycol (34 %) - water | 109 | 5 | 583 | 10 | 61 | 192800 |  | 2 | 10 | 800 | _ | 910 | 18 | 3 phase 400V/50Hz 6P | 58 | 1212 | 206 | X |  |  |  |  | X
773 | X |  |  | 5180 | 2160 | 2150 | 1990 | glycol (34 %) - water | 118 | 5 | 635 | 10 | 69 | 176000 |  | 2 | 10 | 800 | _ | 910 | 18 | 3 phase 400V/50Hz 6P | 58 | 1616 | 276 | X |  |  |  |  | X
774 | X |  |  | 2270 | 2160 | 2150 | 740 | glycol (34 %) - water | 27.2347 | 5 | 145 | 10 |  | 38000 |  | 2 | 4 | 800 | _ | 490 | 0.9 | 3 phase 400V/50Hz 6P | _ | 484 | 84 | X |  |  |  |  | X |  |  |  | X
775 | X |  |  | 2270 | 2160 | 2150 | 740 | glycol (34 %) - water | 39.4434 | 5 | 210 | 10 |  | 64000 |  | 2 | 4 | 800 | _ | 784 | 3.5 | 3 phase 400V/50Hz 6P | _ | 484 | 84 | X |  |  |  |  | X |  |  |  | X
776 | X |  |  | 2270 | 2160 | 2150 | 740 | glycol (34 %) - water | 46.9565 | 5 | 250 | 10 |  | 91000 |  | 2 | 4 | 800 | _ | 980 | 6.6 | 3 phase 400V/50Hz 6P | _ | 484 | 84 | X |  |  |  |  | X |  |  |  | X
777 | X |  |  | 2270 | 2160 | 2150 | 800 | glycol (34 %) - water | 28.9252 | 5 | 154 | 10 |  | 37000 |  | 2 | 4 | 800 | _ | 490 | 0.9 | 3 phase 400V/50Hz 6P | _ | 646 | 112 | X |  |  |  |  | X |  |  |  | X
778 | X |  |  | 2270 | 2160 | 2150 | 800 | glycol (34 %) - water | 42.6365 | 5 | 227 | 10 |  | 58000 |  | 2 | 4 | 800 | _ | 784 | 3.3 | 3 phase 400V/50Hz 6P | _ | 646 | 112 | X |  |  |  |  | X |  |  |  | X
779 | X |  |  | 2270 | 2160 | 2150 | 800 | glycol (34 %) - water | 52.9669 | 5 | 282 | 10 |  | 83000 |  | 2 | 4 | 800 | _ | 980 | 6.6 | 3 phase 400V/50Hz 6P | _ | 646 | 112 | X |  |  |  |  | X |  |  |  | X
780 | X |  |  | 3240 | 2160 | 2150 | 1110 | glycol (34 %) - water | 41.3217 | 5 | 220 | 10 |  | 57000 |  | 2 | 6 | 800 | _ | 490 | 1.4 | 3 phase 400V/50Hz 6P | _ | 726 | 124 | X |  |  |  |  | X |  |  |  | X
781 | X |  |  | 3240 | 2160 | 2150 | 1110 | glycol (34 %) - water | 58.6017 | 5 | 312 | 10 |  | 96000 |  | 2 | 6 | 800 | _ | 784 | 3.5 | 3 phase 400V/50Hz 6P | _ | 726 | 124 | X |  |  |  |  | X |  |  |  | X
782 | X |  |  | 3240 | 2160 | 2150 | 1110 | glycol (34 %) - water | 70.059 | 5 | 373 | 10 |  | 135000 |  | 2 | 6 | 800 | _ | 980 | 9.9 | 3 phase 400V/50Hz 6P | _ | 726 | 124 | X |  |  |  |  | X |  |  |  | X
783 | X |  |  | 3240 | 2160 | 2150 | 1200 | glycol (34 %) - water | 42.2608 | 5 | 225 | 10 |  | 55000 |  | 2 | 6 | 800 | _ | 490 | 1.4 | 3 phase 400V/50Hz 6P | _ | 970 | 166 | X |  |  |  |  | X |  |  |  | X
784 | X |  |  | 3240 | 2160 | 2150 | 1200 | glycol (34 %) - water | 63.8608 | 5 | 340 | 10 |  | 87000 |  | 2 | 6 | 800 | _ | 784 | 4.9 | 3 phase 400V/50Hz 6P | _ | 970 | 166 | X |  |  |  |  | X |  |  |  | X
785 | X |  |  | 3240 | 2160 | 2150 | 1200 | glycol (34 %) - water | 79.6382 | 5 | 424 | 10 |  | 125000 |  | 2 | 6 | 800 | _ | 980 | 9.9 | 3 phase 400V/50Hz 6P | _ | 970 | 166 | X |  |  |  |  | X |  |  |  | X
786 | X |  |  | 4210 | 2160 | 2150 | 1430 | glycol (34 %) - water | 54.8451 | 5 | 292 | 10 |  | 75000 |  | 2 | 8 | 800 | _ | 490 | 1.9 | 3 phase 400V/50Hz 6P | _ | 970 | 166 | X |  |  |  |  | X |  |  |  | X
787 | X |  |  | 4210 | 2160 | 2150 | 1430 | glycol (34 %) - water | 77.9477 | 5 | 415 | 10 |  | 130000 |  | 2 | 8 | 800 | _ | 784 | 7 | 3 phase 400V/50Hz 6P | _ | 970 | 166 | X |  |  |  |  | X |  |  |  | X
788 | X |  |  | 4210 | 2160 | 2150 | 1430 | glycol (34 %) - water | 92.9738 | 5 | 495 | 10 |  | 175000 |  | 2 | 8 | 800 | _ | 980 | 13.1 | 3 phase 400V/50Hz 6P | _ | 970 | 166 | X |  |  |  |  | X |  |  |  | X
789 | X |  |  | 4210 | 2160 | 2150 | 1550 | glycol (34 %) - water | 57.2869 | 5 | 305 | 10 |  | 74000 |  | 2 | 8 | 800 | _ | 490 | 1.9 | 3 phase 400V/50Hz 6P | _ | 1292 | 220 | X |  |  |  |  | X |  |  |  | X
790 | X |  |  | 4210 | 2160 | 2150 | 1550 | glycol (34 %) - water | 85.6486 | 5 | 456 | 10 |  | 115000 |  | 2 | 8 | 800 | _ | 784 | 7 | 3 phase 400V/50Hz 6P | _ | 1292 | 220 | X |  |  |  |  | X |  |  |  | X
791 | X |  |  | 4210 | 2160 | 2150 | 1550 | glycol (34 %) - water | 104.8068 | 5 | 558 | 10 |  | 165000 |  | 2 | 8 | 800 | _ | 980 | 13.1 | 3 phase 400V/50Hz 6P | _ | 1292 | 220 | X |  |  |  |  | X |  |  |  | X
792 | X |  |  | 5180 | 2160 | 2150 | 1850 | glycol (34 %) - water | 68.7443 | 5 | 366 | 10 |  | 94000 |  | 2 | 10 | 800 | _ | 490 | 2.3 | 3 phase 400V/50Hz 6P | _ | 1212 | 206 | X |  |  |  |  | X |  |  |  | X
793 | X |  |  | 5180 | 2160 | 2150 | 1850 | glycol (34 %) - water | 97.6694 | 5 | 520 | 10 |  | 160000 |  | 2 | 10 | 800 | _ | 784 | 8.7 | 3 phase 400V/50Hz 6P | _ | 1212 | 206 | X |  |  |  |  | X |  |  |  | X
794 | X |  |  | 5180 | 2160 | 2150 | 1850 | glycol (34 %) - water | 118.3303 | 5 | 630 | 10 |  | 220000 |  | 2 | 10 | 800 | _ | 980 | 16.4 | 3 phase 400V/50Hz 6P | _ | 1212 | 206 | X |  |  |  |  | X |  |  |  | X
795 | X |  |  | 5180 | 2160 | 2150 | 1990 | glycol (34 %) - water | 70.4347 | 5 | 375 | 10 |  | 92500 |  | 2 | 10 | 800 | _ | 490 | 2.3 | 3 phase 400V/50Hz 6P | _ | 1616 | 276 | X |  |  |  |  | X |  |  |  | X
796 | X |  |  | 5180 | 2160 | 2150 | 1990 | glycol (34 %) - water | 105.5581 | 5 | 562 | 10 |  | 146000 |  | 2 | 10 | 800 | _ | 784 | 8.7 | 3 phase 400V/50Hz 6P | _ | 1616 | 276 | X |  |  |  |  | X |  |  |  | X
797 | X |  |  | 5180 | 2160 | 2150 | 1990 | glycol (34 %) - water | 131.1024 | 5 | 698 | 10 |  | 203000 |  | 2 | 10 | 800 | _ | 980 | 16.4 | 3 phase 400V/50Hz 6P | _ | 1616 | 276 | X |  |  |  |  | X |  |  |  | X
798 | X |  |  | 3250 | 2200 | 2090 | 820 | glycol (34 %) - water | 55 | 5 | 283 | 10 | 63 | 84000 |  | 2 | 4 | 800 | _ | 910 | 6.8 | 3 phase 400V/50Hz 6P | 54 | 880 | 154 | X | X |  |  |  | X
799 | X |  |  | 3250 | 2200 | 2090 | 920 | glycol (34 %) - water | 61 | 5 | 314 | 10 | 69 | 82000 |  | 2 | 4 | 800 | _ | 910 | 6.8 | 3 phase 400V/50Hz 6P | 54 | 1172 | 194 | X | X |  |  |  | X
800 | X |  |  | 3850 | 2200 | 2090 | 1150 | glycol (34 %) - water | 76 | 5 | 391 | 10 | 59 | 122000 |  | 2 | 6 | 800 | _ | 910 | 10.2 | 3 phase 400V/50Hz 6P | 56 | 1084 | 184 | X | X |  |  |  | X
801 | X |  |  | 3850 | 2200 | 2090 | 1290 | glycol (34 %) - water | 82 | 5 | 422 | 10 | 57 | 112000 |  | 2 | 6 | 800 | _ | 910 | 10.2 | 3 phase 400V/50Hz 6P | 56 | 1444 | 236 | X | X |  |  |  | X
802 | X |  |  | 5100 | 2200 | 2105 | 1550 | glycol (34 %) - water | 102 | 5 | 525 | 10 | 58 | 165000 |  | 2 | 8 | 800 | _ | 910 | 13.6 | 3 phase 400V/50Hz 6P | 57 | 1432 | 250 | X | X |  |  |  | X
803 | X |  |  | 5100 | 2200 | 2105 | 1700 | glycol (34 %) - water | 110 | 5 | 569 | 10 | 61 | 153000 |  | 2 | 8 | 800 | _ | 910 | 13.6 | 3 phase 400V/50Hz 6P | 57 | 1908 | 320 | X | X |  |  |  | X
804 | X |  |  | 8100 | 2200 | 2105 | 1850 | glycol (34 %) - water | 131 | 5 | 674 | 10 | 63 | 205000 |  | 2 | 10 | 800 | _ | 910 | 17 | 3 phase 400V/50Hz 6P | 58 | 1964 | 338 | X | X |  |  |  | X
805 | X |  |  | 8100 | 2200 | 2105 | 2100 | glycol (34 %) - water | 143 | 5 | 736 | 10 | 69 | 190000 |  | 2 | 10 | 800 | _ | 910 | 17 | 3 phase 400V/50Hz 6P | 58 | 2616 | 430 | X | X |  |  |  | X
806 | X |  |  | 8700 | 2200 | 2105 | 2140 | glycol (34 %) - water | 152 | 5 | 782 | 10 | 59 | 242000 |  | 2 | 12 | 800 | _ | 910 | 20.4 | 3 phase 400V/50Hz 6P | 59 | 2168 | 368 | X | X |  |  |  | X
807 | X |  |  | 8700 | 2200 | 2105 | 2420 | glycol (34 %) - water | 164 | 5 | 844 | 10 | 57 | 222000 |  | 2 | 12 | 800 | _ | 910 | 20.4 | 3 phase 400V/50Hz 6P | 59 | 2888 | 472 | X | X |  |  |  | X
808 | X |  |  | 9950 | 2200 | 2105 | 2440 | glycol (34 %) - water | 178 | 5 | 916 | 10 | 58 | 282000 |  | 2 | 14 | 800 | _ | 910 | 23.8 | 3 phase 400V/50Hz 6P | 59 | 2516 | 434 | X | X |  |  |  | X
809 | X |  |  | 9950 | 2200 | 2105 | 2760 | glycol (34 %) - water | 192 | 5 | 991 | 10 | 61 | 258000 |  | 2 | 14 | 800 | _ | 910 | 23.8 | 3 phase 400V/50Hz 6P | 59 | 3352 | 556 | X | X |  |  |  | X
810 | X |  |  | 11200 | 2200 | 2105 | 2750 | glycol (34 %) - water | 204 | 5 | 1050 | 10 | 58 | 324000 |  | 2 | 16 | 800 | _ | 910 | 27.2 | 3 phase 400V/50Hz 6P | 60 | 2864 | 500 | X | X |  |  |  | X
811 | X |  |  | 11200 | 2200 | 2105 | 3100 | glycol (34 %) - water | 220 | 5 | 1138 | 10 | 61 | 296000 |  | 2 | 16 | 800 | _ | 910 | 27.2 | 3 phase 400V/50Hz 6P | 60 | 3816 | 640 | X | X |  |  |  | X
812 | X |  |  | 760 | 560 | 690 | 19.7 | glycol (34 %) - water | 0.9 | 5 | 4.6 | 10 | 51 | 2500 |  |  | 1 | 350 | _ | 1400 | 0.13 | 1 phase 230V/50 Hz | 36 | _ | 1.75 | X |  |  |  |  | X
813 | X |  |  | 760 | 560 | 690 | 21.9 | glycol (34 %) - water | 1.2 | 5 | 6 | 10 | 54 | 2200 |  |  | 1 | 350 | _ | 1400 | 0.13 | 1 phase 230V/50 Hz | 36 | _ | 2.63 | X |  |  |  |  | X
814 | X |  |  | 760 | 560 | 690 | 24.3 | glycol (34 %) - water | 1.4 | 5 | 7.4 | 10 | 56 | 2400 |  |  | 1 | 350 | _ | 1400 | 0.13 | 1 phase 230V/50 Hz | 36 | _ | 3.51 | X |  |  |  |  | X
815 | X |  |  | 1310 | 560 | 690 | 30.6 | glycol (34 %) - water | 1.8 | 5 | 9.2 | 10 | 37 | 5000 |  |  | 2 | 350 | _ | 1400 | 0.26 | 1 phase 230V/50 Hz | 39 | _ | 3.39 | X |  |  |  |  | X
816 | X |  |  | 1310 | 560 | 690 | 35 | glycol (34 %) - water | 2.3 | 5 | 12 | 10 | 39 | 4400 |  |  | 2 | 350 | _ | 1400 | 0.26 | 1 phase 230V/50 Hz | 39 | _ | 5.09 | X |  |  |  |  | X
817 | X |  |  | 1310 | 560 | 690 | 39.3 | glycol (34 %) - water | 2.9 | 5 | 15 | 10 | 38 | 4800 |  |  | 2 | 350 | _ | 1400 | 0.26 | 1 phase 230V/50 Hz | 39 | _ | 6.78 | X |  |  |  |  | X
818 | X |  |  | 1860 | 560 | 690 | 41.5 | glycol (34 %) - water | 2.8 | 5 | 14 | 10 | 43 | 7500 |  |  | 3 | 350 | _ | 1400 | 0.39 | 1 phase 230V/50 Hz | 41 | _ | 5.03 | X |  |  |  |  | X
819 | X |  |  | 1860 | 560 | 690 | 47.8 | glycol (34 %) - water | 3.5 | 5 | 18 | 10 | 45 | 6600 |  |  | 3 | 350 | _ | 1400 | 0.39 | 1 phase 230V/50 Hz | 41 | _ | 7.54 | X |  |  |  |  | X
820 | X |  |  | 1860 | 560 | 690 | 54.3 | glycol (34 %) - water | 4.3 | 5 | 22 | 10 | 43 | 7200 |  |  | 3 | 350 | _ | 1400 | 0.39 | 1 phase 230V/50 Hz | 41 | _ | 10.05 | X |  |  |  |  | X
821 | X |  |  | 1310 | 1110 | 690 | 63 | glycol (34 %) - water | 3.6 | 5 | 18 | 10 | 37 | 10000 |  |  | 4 | 350 | _ | 1400 | 0.52 | 1 phase 230V/50 Hz | 42 | _ | 6.78 | X |  |  |  |  | X
822 | X |  |  | 1310 | 1110 | 690 | 72.1 | glycol (34 %) - water | 4.6 | 5 | 24 | 10 | 39 | 8800 |  |  | 4 | 350 | _ | 1400 | 0.52 | 1 phase 230V/50 Hz | 42 | _ | 10.17 | X |  |  |  |  | X
823 | X |  |  | 1310 | 1110 | 690 | 81 | glycol (34 %) - water | 5.7 | 5 | 30 | 10 | 47 | 9600 |  |  | 4 | 350 | _ | 1400 | 0.52 | 1 phase 230V/50 Hz | 42 | _ | 13.56 | X |  |  |  |  | X
824 | X |  |  | 1860 | 1110 | 690 | 85.5 | glycol (34 %) - water | 5.4 | 5 | 28 | 10 | 38 | 15000 |  |  | 6 | 350 | _ | 1400 | 0.78 | 1 phase 230V/50 Hz | 44 | _ | 10.05 | X |  |  |  |  | X
825 | X |  |  | 1860 | 1110 | 690 | 98.5 | glycol (34 %) - water | 6.6 | 5 | 38 | 10 | 39 | 13200 |  |  | 6 | 350 | _ | 1400 | 0.78 | 1 phase 230V/50 Hz | 44 | _ | 15.08 | X |  |  |  |  | X
826 | X |  |  | 1860 | 1110 | 690 | 111.8 | glycol (34 %) - water | 8.1 | 5 | 47 | 10 | 47 | 14400 |  |  | 6 | 350 | _ | 1400 | 0.78 | 1 phase 230V/50 Hz | 44 | _ | 20.11 | X |  |  |  |  | X
827 | X |  |  | 1105 | 773 | 870 | 70 | glycol (34 %) - water | 3.2 | 5 | 16 | 10 | 26 | 7360 |  |  | 1 | 500 | _ | 1210 | 0.77 | 1 phase 230V/50 Hz | 45 | 34.5 | 6.1 | X |  |  |  |  | X
828 | X |  |  | 1105 | 773 | 870 | 74 | glycol (34 %) - water | 3.8 | 5 | 20 | 10 | 31 | 7030 |  |  | 1 | 500 | _ | 1210 | 0.77 | 1 phase 230V/50 Hz | 45 | 46 | 8.1 | X |  |  |  |  | X
829 | X |  |  | 1105 | 773 | 870 | 78 | glycol (34 %) - water | 4.2 | 5 | 22 | 10 | 33 | 6745 |  |  | 1 | 500 | _ | 1210 | 0.77 | 1 phase 230V/50 Hz | 45 | 57.5 | 9.9 | X |  |  |  |  | X
830 | X |  |  | 2045 | 773 | 870 | 107 | glycol (34 %) - water | 5 | 5 | 26 | 10 | 40 | 15200 |  |  | 2 | 500 | _ | 1210 | 1.54 | 1 phase 230V/50 Hz | 48 | 47.6 | 7.9 | X |  |  |  |  | X
831 | X |  |  | 2045 | 773 | 870 | 116 | glycol (34 %) - water | 6.6 | 5 | 34 | 10 | 32 | 14720 |  |  | 2 | 500 | _ | 1210 | 1.54 | 1 phase 230V/50 Hz | 48 | 71.4 | 12.2 | X |  |  |  |  | X
832 | X |  |  | 2045 | 773 | 870 | 125 | glycol (34 %) - water | 7.9 | 5 | 41 | 10 | 47 | 14060 |  |  | 2 | 500 | _ | 1210 | 1.54 | 1 phase 230V/50 Hz | 48 | 95.2 | 16.1 | X |  |  |  |  | X
833 | X |  |  | 2045 | 773 | 870 | 134 | glycol (34 %) - water | 8.7 | 5 | 45 | 10 | 37 | 13490 |  |  | 2 | 500 | _ | 1210 | 1.54 | 1 phase 230V/50 Hz | 50 | 119 | 19.7 | X |  |  |  |  | X
834 | X |  |  | 2985 | 773 | 870 | 162 | glycol (34 %) - water | 10.1 | 5 | 52 | 10 | 39 | 22080 |  |  | 3 | 500 | _ | 1210 | 2.31 | 1 phase 230V/50 Hz | 50 | 108.2 | 18.1 | X |  |  |  |  | X
835 | X |  |  | 2985 | 773 | 870 | 175 | glycol (34 %) - water | 11.8 | 5 | 61 | 10 | 34 | 21090 |  |  | 3 | 500 | _ | 1210 | 2.31 | 1 phase 230V/50 Hz | 50 | 144.3 | 24 | X |  |  |  |  | X
836 | X |  |  | 2985 | 773 | 870 | 188 | glycol (34 %) - water | 13.1 | 5 | 67 | 10 | 27 | 20235 |  |  | 3 | 500 | _ | 1210 | 2.31 | 1 phase 230V/50 Hz | 51 | 180.4 | 29.5 | X |  |  |  |  | X
837 | X |  |  | 3925 | 773 | 870 | 206 | glycol (34 %) - water | 13.3 | 5 | 69 | 10 | 30 | 29440 |  |  | 4 | 500 | _ | 1210 | 3.08 | 1 phase 230V/50 Hz | 51 | 142.8 | 23.9 | X |  |  |  |  | X
838 | X |  |  | 3925 | 773 | 870 | 224 | glycol (34 %) - water | 15.6 | 5 | 80 | 10 | 23 | 28120 |  |  | 4 | 500 | _ | 1210 | 3.08 | 1 phase 230V/50 Hz | 51 | 190.3 | 31.6 | X |  |  |  |  | X
839 | X |  |  | 3925 | 773 | 870 | 242 | glycol (34 %) - water | 17.9 | 5 | 92 | 10 | 56 | 26980 |  |  | 4 | 500 | _ | 1210 | 3.08 | 1 phase 230V/50 Hz | 51 | 237.9 | 38.8 | X |  |  |  |  | X
840 | X |  |  | 2985 | 773 | 870 | 324 | glycol (34 %) - water | 20.1 | 5 | 104 | 10 | 39 | 44160 |  |  | 6 | 500 | _ | 1210 | 4.62 | 1 phase 230V/50 Hz | 53 | 216.4 | 37.2 | X |  |  |  |  | X
841 | X |  |  | 2985 | 773 | 870 | 350 | glycol (34 %) - water | 23.6 | 5 | 122 | 10 | 34 | 42180 |  |  | 6 | 500 | _ | 1210 | 4.62 | 1 phase 230V/50 Hz | 53 | 288.6 | 50.1 | X |  |  |  |  | X
842 | X |  |  | 2985 | 773 | 870 | 376 | glycol (34 %) - water | 26.1 | 5 | 135 | 10 | 27 | 40470 |  |  | 6 | 500 | _ | 1210 | 4.62 | 1 phase 230V/50 Hz | 53 | 360.8 | 61.1 | X |  |  |  |  | X
843 | X |  |  | 3925 | 773 | 870 | 412 | glycol (34 %) - water | 26.7 | 5 | 137 | 10 | 30 | 58880 |  |  | 8 | 500 | _ | 1210 | 6.16 | 1 phase 230V/50 Hz | 54 | 285.6 | 49 | X |  |  |  |  | X
844 | X |  |  | 3925 | 773 | 870 | 448 | glycol (34 %) - water | 31.1 | 5 | 160 | 10 | 23 | 56240 |  |  | 8 | 500 | _ | 1210 | 6.16 | 1 phase 230V/50 Hz | 54 | 380.6 | 64.4 | X |  |  |  |  | X
845 | X |  |  | 3925 | 773 | 870 | 484 | glycol (34 %) - water | 35.8 | 5 | 185 | 10 | 56 | 53960 |  |  | 8 | 500 | _ | 1210 | 6.16 | 1 phase 230V/50 Hz | 54 | 475.8 | 81.9 | X |  |  |  |  | X
846 | X |  |  | 1340 | 1374 | 1180 | 108 | glycol (34 %) - water | 4.5 | 5 | 23 | 10 | 22 | 9550 |  |  | 1 | 630 | _ | 900 | 0.69 | 3 phase 400V/50Hz 6P | 49 | 57.2 | 8.8 | X |  |  |  |  | X
847 | X |  |  | 1340 | 1374 | 1180 | 115 | glycol (34 %) - water | 5.4 | 5 | 28 | 10 | 42 | 9150 |  |  | 1 | 630 | _ | 900 | 0.69 | 3 phase 400V/50Hz 6P | 49 | 76.3 | 11.8 | X |  |  |  |  | X
848 | X |  |  | 1340 | 1374 | 1180 | 123 | glycol (34 %) - water | 5.9 | 5 | 31 | 10 | 46 | 8700 |  |  | 1 | 630 | _ | 900 | 0.69 | 3 phase 400V/50Hz 6P | 49 | 95.3 | 14.7 | X |  |  |  |  | X
849 | X |  |  | 2500 | 1374 | 1180 | 182 | glycol (34 %) - water | 9.4 | 5 | 48 | 10 | 45 | 19100 |  |  | 2 | 630 | _ | 900 | 1.38 | 3 phase 400V/50Hz 6P | 52 | 117.5 | 17.8 | X |  |  |  |  | X
850 | X |  |  | 2500 | 1374 | 1180 | 196 | glycol (34 %) - water | 10.9 | 5 | 56 | 10 | 35 | 18300 |  |  | 2 | 630 | _ | 900 | 1.38 | 3 phase 400V/50Hz 6P | 52 | 156.6 | 23.7 | X |  |  |  |  | X
851 | X |  |  | 2500 | 1374 | 1180 | 211 | glycol (34 %) - water | 12.1 | 5 | 62 | 10 | 49 | 17400 |  |  | 2 | 630 | _ | 900 | 1.38 | 3 phase 400V/50Hz 6P | 52 | 195.8 | 29.7 | X |  |  |  |  | X
852 | X |  |  | 3660 | 1374 | 1180 | 260 | glycol (34 %) - water | 14.3 | 5 | 74 | 10 | 56 | 28650 |  |  | 3 | 630 | _ | 900 | 2.07 | 3 phase 400V/50Hz 6P | 54 | 177.8 | 26.8 | X |  |  |  |  | X
853 | X |  |  | 3660 | 1374 | 1180 | 282 | glycol (34 %) - water | 16.6 | 5 | 85 | 10 | 44 | 27450 |  |  | 3 | 630 | _ | 900 | 2.07 | 3 phase 400V/50Hz 6P | 54 | 237 | 35.7 | X |  |  |  |  | X
854 | X |  |  | 3660 | 1374 | 1180 | 304 | glycol (34 %) - water | 18.1 | 5 | 93 | 10 | 36 | 26100 |  |  | 3 | 630 | _ | 900 | 2.07 | 3 phase 400V/50Hz 6P | 54 | 296.3 | 44.7 | X |  |  |  |  | X
855 | X |  |  | 4820 | 1374 | 1180 | 333 | glycol (34 %) - water | 18.9 | 5 | 98 | 10 | 42 | 38200 |  |  | 4 | 630 | _ | 900 | 2.76 | 3 phase 400V/50Hz 6P | 55 | 238 | 35.8 | X |  |  |  |  | X
856 | X |  |  | 4820 | 1374 | 1180 | 363 | glycol (34 %) - water | 21.9 | 5 | 113 | 10 | 32 | 36600 |  |  | 4 | 630 | _ | 900 | 2.76 | 3 phase 400V/50Hz 6P | 55 | 317.4 | 47.7 | X |  |  |  |  | X
857 | X |  |  | 4820 | 1374 | 1180 | 393 | glycol (34 %) - water | 23.8 | 5 | 123 | 10 | 25 | 34800 |  |  | 4 | 630 | _ | 900 | 2.76 | 3 phase 400V/50Hz 6P | 55 | 396.8 | 59.6 | X |  |  |  |  | X
858 | X |  |  | 3660 | 1374 | 1180 | 520 | glycol (34 %) - water | 28.6 | 5 | 147 | 10 | 56 | 57300 |  |  | 6 | 630 | _ | 900 | 4.14 | 3 phase 400V/50Hz 6P | 57 | 355.6 | 53.6 | X |  |  |  |  | X
859 | X |  |  | 3660 | 1374 | 1180 | 564 | glycol (34 %) - water | 33.1 | 5 | 171 | 10 | 44 | 54900 |  |  | 6 | 630 | _ | 900 | 4.14 | 3 phase 400V/50Hz 6P | 57 | 474 | 71.4 | X |  |  |  |  | X
860 | X |  |  | 3660 | 1374 | 1180 | 608 | glycol (34 %) - water | 36.1 | 5 | 186 | 10 | 36 | 52200 |  |  | 6 | 630 | _ | 900 | 4.14 | 3 phase 400V/50Hz 6P | 57 | 592.6 | 89.4 | X |  |  |  |  | X
861 | X |  |  | 4820 | 1374 | 1180 | 666 | glycol (34 %) - water | 37.8 | 5 | 195 | 10 | 42 | 76400 |  |  | 8 | 630 | _ | 900 | 5.52 | 3 phase 400V/50Hz 6P | 58 | 476 | 71.6 | X |  |  |  |  | X
862 | X |  |  | 4820 | 1374 | 1180 | 726 | glycol (34 %) - water | 43.9 | 5 | 226 | 10 | 32 | 73200 |  |  | 8 | 630 | _ | 900 | 5.52 | 3 phase 400V/50Hz 6P | 58 | 634.8 | 95.4 | X |  |  |  |  | X
863 | X |  |  | 4820 | 1374 | 1180 | 786 | glycol (34 %) - water | 47.7 | 5 | 246 | 10 | 25 | 69600 |  |  | 8 | 630 | _ | 900 | 5.52 | 3 phase 400V/50Hz 6P | 58 | 793.6 | 119.2 | X |  |  |  |  | X
864 | X |  |  | 1663 | 1374 | 1180 | 170 | glycol (34 %) - water | 9.2 | 5 | 47 | 10 | 48 | 20400 |  |  | 1 | 910 | _ | 885 | 1.45 | 3 phase 400V/50Hz 6P | 56 | 98.8 | 17.9 | X |  |  |  |  | X
865 | X |  |  | 1663 | 1374 | 1180 | 181 | glycol (34 %) - water | 10.7 | 5 | 55 | 10 | 37 | 19350 |  |  | 1 | 910 | _ | 885 | 1.45 | 3 phase 400V/50Hz 6P | 56 | 131.8 | 23.2 | X |  |  |  |  | X
866 | X |  |  | 1663 | 1374 | 1180 | 203 | glycol (34 %) - water | 12.7 | 5 | 65 | 10 | 37 | 17700 |  |  | 1 | 910 | _ | 885 | 1.45 | 3 phase 400V/50Hz 6P | 56 | 197.7 | 33.6 | X |  |  |  |  | X
867 | X |  |  | 3063 | 1374 | 1180 | 295 | glycol (34 %) - water | 18.6 | 5 | 96 | 10 | 42 | 40800 |  |  | 2 | 910 | _ | 885 | 2.9 | 3 phase 400V/50Hz 6P | 59 | 197.7 | 34.6 | X |  |  |  |  | X
868 | X |  |  | 3063 | 1374 | 1180 | 320 | glycol (34 %) - water | 21.6 | 5 | 111 | 10 | 33 | 38700 |  |  | 2 | 910 | _ | 885 | 2.9 | 3 phase 400V/50Hz 6P | 59 | 263.5 | 46.3 | X |  |  |  |  | X
869 | X |  |  | 3063 | 1374 | 1180 | 370 | glycol (34 %) - water | 25.9 | 5 | 133 | 10 | 47 | 35400 |  |  | 2 | 910 | _ | 885 | 2.9 | 3 phase 400V/50Hz 6P | 59 | 395.3 | 67.3 | X |  |  |  |  | X
870 | X |  |  | 4493 | 1374 | 1180 | 418 | glycol (34 %) - water | 27.9 | 5 | 144 | 10 | 40 | 61200 |  |  | 3 | 910 | _ | 885 | 4.35 | 3 phase 400V/50Hz 6P | 61 | 296.5 | 51.4 | X |  |  |  |  | X
871 | X |  |  | 4493 | 1374 | 1180 | 457 | glycol (34 %) - water | 32.5 | 5 | 168 | 10 | 31 | 58050 |  |  | 3 | 910 | _ | 885 | 4.35 | 3 phase 400V/50Hz 6P | 61 | 395.3 | 67.4 | X |  |  |  |  | X
872 | X |  |  | 4493 | 1374 | 1180 | 535 | glycol (34 %) - water | 37.8 | 5 | 195 | 10 | 20 | 53100 |  |  | 3 | 910 | _ | 885 | 4.35 | 3 phase 400V/50Hz 6P | 61 | 593 | 101.8 | X |  |  |  |  | X
873 | X |  |  | 3063 | 1374 | 1180 | 590 | glycol (34 %) - water | 37 | 5 | 191 | 10 | 40 | 81600 |  |  | 4 | 910 | _ | 885 | 5.8 | 3 phase 400V/50Hz 6P | 62 | 395.4 | 76.9 | X |  |  |  |  | X
874 | X |  |  | 3063 | 1374 | 1180 | 640 | glycol (34 %) - water | 43.2 | 5 | 223 | 10 | 33 | 77400 |  |  | 4 | 910 | _ | 885 | 5.8 | 3 phase 400V/50Hz 6P | 62 | 527 | 98.4 | X |  |  |  |  | X
875 | X |  |  | 3063 | 1374 | 1180 | 740 | glycol (34 %) - water | 51.7 | 5 | 267 | 10 | 47 | 70800 |  |  | 4 | 910 | _ | 885 | 5.8 | 3 phase 400V/50Hz 6P | 62 | 790.6 | 140.2 | X |  |  |  |  | X
876 | X |  |  | 4493 | 1374 | 1180 | 836 | glycol (34 %) - water | 56 | 5 | 289 | 10 | 41 | 122400 |  |  | 6 | 910 | _ | 885 | 8.7 | 3 phase 400V/50Hz 6P | 64 | 593 | 112.6 | X |  |  |  |  | X
877 | X |  |  | 4493 | 1374 | 1180 | 914 | glycol (34 %) - water | 65 | 5 | 335 | 10 | 31 | 116100 |  |  | 6 | 910 | _ | 885 | 8.7 | 3 phase 400V/50Hz 6P | 64 | 790.6 | 144.7 | X |  |  |  |  | X
878 | X |  |  | 4493 | 1374 | 1180 | 1070 | glycol (34 %) - water | 75.7 | 5 | 390 | 10 | 20 | 106200 |  |  | 6 | 910 | _ | 885 | 8.7 | 3 phase 400V/50Hz 6P | 64 | 1186 | 207.7 | X |  |  |  |  | X
879 | X |  |  | 1878 | 1252 | 1340 | 170 | glycol (34 %) - water | 10.1426 | 5 | 54 | 10 | 33 | 18750 |  |  | 1 | 800 | _ | 895 | 1.8 | 3 phase 400V/50Hz 6P | 52 | _ | _ | X |  |  |  |  | X
880 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 12.0209 | 5 | 64 | 10 | 48 | 17950 |  |  | 1 | 800 | _ | 895 | 1.8 | 3 phase 400V/50Hz 6P | 52 | _ | _ | X |  |  |  |  | X
881 | X |  |  | 3543 | 1252 | 1340 | 300 | glycol (34 %) - water | 20.473 | 5 | 109 | 10 | 34 | 36200 |  |  | 2 | 800 | _ | 895 | 3.6 | 3 phase 400V/50Hz 6P | 55 | _ | _ | X |  |  |  |  | X
882 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 22.9148 | 5 | 122 | 10 | 25 | 33600 |  |  | 2 | 800 | _ | 895 | 3.6 | 3 phase 400V/50Hz 6P | 55 | _ | _ | X |  |  |  |  | X
883 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 30.9913 | 5 | 165 | 10 | 32 | 54300 |  |  | 3 | 800 | _ | 895 | 5.4 | 3 phase 400V/50Hz 6P | 57 | _ | _ | X |  |  |  |  | X
884 | X |  |  | 5208 | 1252 | 1340 | 470 | glycol (34 %) - water | 34.9356 | 5 | 186 | 10 | 24 | 50650 |  |  | 3 | 800 | _ | 895 | 5.4 | 3 phase 400V/50Hz 6P | 57 | _ | _ | X |  |  |  |  | X
885 | X |  |  | 3543 | 1252 | 1340 | 600 | glycol (34 %) - water | 41.1339 | 5 | 219 | 10 | 34 | 72400 |  |  | 4 | 800 | _ | 895 | 7.2 | 3 phase 400V/50Hz 6P | 58 | _ | _ | X |  |  |  |  | X
886 | X |  |  | 3543 | 1252 | 1340 | 670 | glycol (34 %) - water | 46.0173 | 5 | 245 | 10 | 25 | 67200 |  |  | 4 | 800 | _ | 895 | 7.2 | 3 phase 400V/50Hz 6P | 58 | _ | _ | X |  |  |  |  | X
887 | X |  |  | 5208 | 1252 | 1340 | 850 | glycol (34 %) - water | 62.1704 | 5 | 331 | 10 | 32 | 108600 |  |  | 6 | 800 | _ | 895 | 10.8 | 3 phase 400V/50Hz 6P | 59 | _ | _ | X |  |  |  |  | X
888 | X |  |  | 5208 | 1252 | 1340 | 940 | glycol (34 %) - water | 69.6834 | 5 | 371 | 10 | 24 | 101300 |  |  | 6 | 800 | _ | 895 | 10.8 | 3 phase 400V/50Hz 6P | 59 | _ | _ | X |  |  |  |  | X
889 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 10.7061 | 5 | 57 | 10 | 36 | 20000 |  |  | 1 | 800 | _ | 980 | 1.75 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X |  |  |  | X
890 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 9.9548 | 5 | 53 | 10 | 31 | 17850 |  |  | 1 | 800 | _ | 882 | 1.3 | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  |  | X |  |  |  | X
891 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 9.2035 | 5 | 49 | 10 | 27 | 15750 |  |  | 1 | 800 | _ | 784 | 0.9 | 3 phase 400V/50Hz | 47 | _ | _ | X |  |  |  |  | X |  |  |  | X
892 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 8.2643 | 5 | 44 | 10 | 22 | 13550 |  |  | 1 | 800 | _ | 686 | 0.6 | 3 phase 400V/50Hz | 44 | _ | _ | X |  |  |  |  | X |  |  |  | X
893 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 7.3252 | 5 | 39 | 10 | 19 | 11450 |  |  | 1 | 800 | _ | 588 | 0.37 | 3 phase 400V/50Hz | 41 | _ | _ | X |  |  |  |  | X |  |  |  | X
894 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 6.3861 | 5 | 34 | 10 | 14 | 9450 |  |  | 1 | 800 | _ | 490 | 0.22 | 3 phase 400V/50Hz | 37 | _ | _ | X |  |  |  |  | X |  |  |  | X
895 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 5.2591 | 5 | 28 | 10 | 9 | 7450 |  |  | 1 | 800 | _ | 392 | 0.13 | 3 phase 400V/50Hz | 33 | _ | _ | X |  |  |  |  | X |  |  |  | X
896 | X |  |  | 1878 | 1252 | 1340 | 185 | glycol (34 %) - water | 3.9443 | 5 | 21 | 10 | 5 | 5300 |  |  | 1 | 800 | _ | 294 | 0.05 | 3 phase 400V/50Hz | 29 | _ | _ | X |  |  |  |  | X |  |  |  | X
897 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 12.3965 | 5 | 66 | 10 | 49 | 18900 |  |  | 1 | 800 | _ | 980 | 1.75 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X
898 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 11.2696 | 5 | 60 | 10 | 41 | 16850 |  |  | 1 | 800 | _ | 882 | 1.3 | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  |  | X
899 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 10.3304 | 5 | 55 | 10 | 35 | 14850 |  |  | 1 | 800 | _ | 784 | 0.9 | 3 phase 400V/50Hz | 47 | _ | _ | X |  |  |  |  | X
900 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 9.2035 | 5 | 49 | 10 | 29 | 12800 |  |  | 1 | 800 | _ | 686 | 0.6 | 3 phase 400V/50Hz | 44 | _ | _ | X |  |  |  |  | X
901 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 7.8887 | 5 | 42 | 10 | 23 | 10750 |  |  | 1 | 800 | _ | 588 | 0.37 | 3 phase 400V/50Hz | 41 | _ | _ | X |  |  |  |  | X
902 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 6.7617 | 5 | 36 | 10 | 17 | 8850 |  |  | 1 | 800 | _ | 490 | 0.22 | 3 phase 400V/50Hz | 37 | _ | _ | X |  |  |  |  | X
903 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 5.4469 | 5 | 29 | 10 | 11 | 6950 |  |  | 1 | 800 | _ | 392 | 0.13 | 3 phase 400V/50Hz | 33 | _ | _ | X |  |  |  |  | X
904 | X |  |  | 1878 | 1252 | 1340 | 200 | glycol (34 %) - water | 4.1322 | 5 | 22 | 10 | 6 | 4950 |  |  | 1 | 800 | _ | 294 | 0.05 | 3 phase 400V/50Hz | 29 | _ | _ | X |  |  |  |  | X
905 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 21.4121 | 5 | 114 | 10 | 36 | 38650 |  |  | 2 | 800 | _ | 980 | 3.5 | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  |  | X
906 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 19.7217 | 5 | 105 | 10 | 31 | 34350 |  |  | 2 | 800 | _ | 882 | 2.6 | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  |  | X
907 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 18.0313 | 5 | 96 | 10 | 28 | 30250 |  |  | 2 | 800 | _ | 784 | 1.8 | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  |  | X
908 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 16.3408 | 5 | 87 | 10 | 23 | 26000 |  |  | 2 | 800 | _ | 686 | 1.2 | 3 phase 400V/50Hz | 47 | _ | _ | X |  |  |  |  | X
909 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 14.4626 | 5 | 77 | 10 | 19 | 21850 |  |  | 2 | 800 | _ | 588 | 0.74 | 3 phase 400V/50Hz | 44 | _ | _ | X |  |  |  |  | X
910 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 12.5843 | 5 | 67 | 10 | 16 | 17900 |  |  | 2 | 800 | _ | 490 | 0.44 | 3 phase 400V/50Hz | 40 | _ | _ | X |  |  |  |  | X
911 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 10.5182 | 5 | 56 | 10 | 11 | 14050 |  |  | 2 | 800 | _ | 392 | 0.26 | 3 phase 400V/50Hz | 36 | _ | _ | X |  |  |  |  | X
912 | X |  |  | 3543 | 1252 | 1340 | 305 | glycol (34 %) - water | 8.0765 | 5 | 43 | 10 | 6 | 9950 |  |  | 2 | 800 | _ | 294 | 0.1 | 3 phase 400V/50Hz | 32 | _ | _ | X |  |  |  |  | X
913 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 24.0417 | 5 | 128 | 10 | 26 | 35750 |  |  | 2 | 800 | _ | 980 | 3.5 | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  |  | X
914 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 21.6 | 5 | 115 | 10 | 23 | 31750 |  |  | 2 | 800 | _ | 882 | 2.6 | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  |  | X
915 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 19.3461 | 5 | 103 | 10 | 20 | 27850 |  |  | 2 | 800 | _ | 784 | 1.8 | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  |  | X
916 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 17.28 | 5 | 92 | 10 | 16 | 23900 |  |  | 2 | 800 | _ | 686 | 1.2 | 3 phase 400V/50Hz | 47 | _ | _ | X |  |  |  |  | X
917 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 15.2139 | 5 | 81 | 10 | 13 | 20100 |  |  | 2 | 800 | _ | 588 | 0.74 | 3 phase 400V/50Hz | 44 | _ | _ | X |  |  |  |  | X
918 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 12.7722 | 5 | 68 | 10 | 10 | 16300 |  |  | 2 | 800 | _ | 490 | 0.44 | 3 phase 400V/50Hz | 40 | _ | _ | X |  |  |  |  | X
919 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 10.5182 | 5 | 56 | 10 | 7 | 12700 |  |  | 2 | 800 | _ | 392 | 0.26 | 3 phase 400V/50Hz | 36 | _ | _ | X |  |  |  |  | X
920 | X |  |  | 3543 | 1252 | 1340 | 335 | glycol (34 %) - water | 7.7009 | 5 | 41 | 10 | 3 | 9050 |  |  | 2 | 800 | _ | 294 | 0.1 | 3 phase 400V/50Hz | 32 | _ | _ | X |  |  |  |  | X
921 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 32.306 | 5 | 172 | 10 | 35 | 58200 |  |  | 3 | 800 | _ | 980 | 5.25 | 3 phase 400V/50Hz | 57 | _ | _ | X |  |  |  |  | X
922 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 30.24 | 5 | 161 | 10 | 30 | 51750 |  |  | 3 | 800 | _ | 882 | 3.9 | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  |  | X
923 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 28.1739 | 5 | 150 | 10 | 26 | 45550 |  |  | 3 | 800 | _ | 784 | 2.7 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X
924 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 25.1687 | 5 | 134 | 10 | 22 | 39150 |  |  | 3 | 800 | _ | 686 | 1.8 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X
925 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 22.9148 | 5 | 122 | 10 | 18 | 32950 |  |  | 3 | 800 | _ | 588 | 1.11 | 3 phase 400V/50Hz | 46 | _ | _ | X |  |  |  |  | X
926 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 19.7217 | 5 | 105 | 10 | 14 | 27000 |  |  | 3 | 800 | _ | 490 | 0.66 | 3 phase 400V/50Hz | 42 | _ | _ | X |  |  |  |  | X
927 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 16.3408 | 5 | 87 | 10 | 9 | 21150 |  |  | 3 | 800 | _ | 392 | 0.39 | 3 phase 400V/50Hz | 38 | _ | _ | X |  |  |  |  | X
928 | X |  |  | 5208 | 1252 | 1340 | 425 | glycol (34 %) - water | 12.3965 | 5 | 66 | 10 | 5 | 15050 |  |  | 3 | 800 | _ | 294 | 0.15 | 3 phase 400V/50Hz | 34 | _ | _ | X |  |  |  |  | X
929 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 36.4382 | 5 | 194 | 10 | 26 | 53900 |  |  | 3 | 800 | _ | 980 | 5.25 | 3 phase 400V/50Hz | 57 | _ | _ | X |  |  |  |  | X
930 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 33.6208 | 5 | 179 | 10 | 22 | 47900 |  |  | 3 | 800 | _ | 882 | 3.9 | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  |  | X
931 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 30.4278 | 5 | 162 | 10 | 19 | 42000 |  |  | 3 | 800 | _ | 784 | 2.7 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X
932 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 27.0469 | 5 | 144 | 10 | 16 | 36050 |  |  | 3 | 800 | _ | 686 | 1.8 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X
933 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 23.6661 | 5 | 126 | 10 | 13 | 30300 |  |  | 3 | 800 | _ | 588 | 1.11 | 3 phase 400V/50Hz | 46 | _ | _ | X |  |  |  |  | X
934 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 20.0974 | 5 | 107 | 10 | 10 | 24600 |  |  | 3 | 800 | _ | 490 | 0.66 | 3 phase 400V/50Hz | 42 | _ | _ | X |  |  |  |  | X
935 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 16.153 | 5 | 86 | 10 | 7 | 19150 |  |  | 3 | 800 | _ | 392 | 0.39 | 3 phase 400V/50Hz | 38 | _ | _ | X |  |  |  |  | X
936 | X |  |  | 5208 | 1252 | 1340 | 465 | glycol (34 %) - water | 12.0209 | 5 | 64 | 10 | 4 | 13700 |  |  | 3 | 800 | _ | 294 | 0.15 | 3 phase 400V/50Hz | 34 | _ | _ | X |  |  |  |  | X
937 | X |  |  | 3543 | 1252 | 1340 | 595 | glycol (34 %) - water | 42.8243 | 5 | 228 | 10 | 36 | 77300 |  |  | 4 | 800 | _ | 980 | 7 | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  |  | X
938 | X |  |  | 3543 | 1252 | 1340 | 595 | glycol (34 %) - water | 39.4434 | 5 | 210 | 10 | 31 | 68700 |  |  | 4 | 800 | _ | 882 | 5.2 | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  |  | X
939 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 48.0834 | 5 | 256 | 10 | 26 | 71500 |  |  | 4 | 800 | _ | 980 | 7 | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  |  | X
940 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 43.1999 | 5 | 230 | 10 | 23 | 63500 |  |  | 4 | 800 | _ | 882 | 5.2 | 3 phase 400V/50Hz | 56 | _ | _ | X |  |  |  |  | X
941 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 38.6921 | 5 | 206 | 10 | 20 | 55700 |  |  | 4 | 800 | _ | 784 | 3.6 | 3 phase 400V/50Hz | 53 | _ | _ | X |  |  |  |  | X
942 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 34.56 | 5 | 184 | 10 | 16 | 47800 |  |  | 4 | 800 | _ | 686 | 2.4 | 3 phase 400V/50Hz | 50 | _ | _ | X |  |  |  |  | X
943 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 30.4278 | 5 | 162 | 10 | 13 | 40200 |  |  | 4 | 800 | _ | 588 | 1.48 | 3 phase 400V/50Hz | 47 | _ | _ | X |  |  |  |  | X
944 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 25.5443 | 5 | 136 | 10 | 10 | 32600 |  |  | 4 | 800 | _ | 490 | 0.88 | 3 phase 400V/50Hz | 43 | _ | _ | X |  |  |  |  | X
945 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 21.0365 | 5 | 112 | 10 | 7 | 25400 |  |  | 4 | 800 | _ | 392 | 0.52 | 3 phase 400V/50Hz | 39 | _ | _ | X |  |  |  |  | X
946 | X |  |  | 3543 | 1252 | 1340 | 655 | glycol (34 %) - water | 15.4017 | 5 | 82 | 10 | 3 | 18100 |  |  | 4 | 800 | _ | 294 | 0.2 | 3 phase 400V/50Hz | 35 | _ | _ | X |  |  |  |  | X
947 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 64.7999 | 5 | 345 | 10 | 35 | 116400 |  |  | 6 | 800 | _ | 980 | 10.5 | 3 phase 400V/50Hz | 60 | _ | _ | X |  |  |  |  | X
948 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 60.4799 | 5 | 322 | 10 | 30 | 103500 |  |  | 6 | 800 | _ | 882 | 7.8 | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  |  | X
949 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 56.3478 | 5 | 300 | 10 | 26 | 91100 |  |  | 6 | 800 | _ | 784 | 5.4 | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  |  | X
950 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 50.3373 | 5 | 268 | 10 | 22 | 78300 |  |  | 6 | 800 | _ | 686 | 3.6 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X
951 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 45.8295 | 5 | 244 | 10 | 18 | 65900 |  |  | 6 | 800 | _ | 588 | 2.22 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X
952 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 39.4434 | 5 | 210 | 10 | 14 | 54000 |  |  | 6 | 800 | _ | 490 | 1.32 | 3 phase 400V/50Hz | 45 | _ | _ | X |  |  |  |  | X
953 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 32.6817 | 5 | 174 | 10 | 9 | 42300 |  |  | 6 | 800 | _ | 392 | 0.78 | 3 phase 400V/50Hz | 41 | _ | _ | X |  |  |  |  | X
954 | X |  |  | 5208 | 1252 | 1340 | 835 | glycol (34 %) - water | 24.793 | 5 | 132 | 10 | 5 | 30100 |  |  | 6 | 800 | _ | 294 | 0.3 | 3 phase 400V/50Hz | 37 | _ | _ | X |  |  |  |  | X
955 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 72.6886 | 5 | 387 | 10 | 26 | 107800 |  |  | 6 | 800 | _ | 980 | 10.5 | 3 phase 400V/50Hz | 60 | _ | _ | X |  |  |  |  | X
956 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 67.2417 | 5 | 358 | 10 | 22 | 95800 |  |  | 6 | 800 | _ | 882 | 7.8 | 3 phase 400V/50Hz | 58 | _ | _ | X |  |  |  |  | X
957 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 60.8556 | 5 | 324 | 10 | 19 | 84000 |  |  | 6 | 800 | _ | 784 | 5.4 | 3 phase 400V/50Hz | 55 | _ | _ | X |  |  |  |  | X
958 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 54.0938 | 5 | 288 | 10 | 16 | 72100 |  |  | 6 | 800 | _ | 686 | 3.6 | 3 phase 400V/50Hz | 52 | _ | _ | X |  |  |  |  | X
959 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 47.3321 | 5 | 252 | 10 | 13 | 60600 |  |  | 6 | 800 | _ | 588 | 2.22 | 3 phase 400V/50Hz | 49 | _ | _ | X |  |  |  |  | X
960 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 40.1947 | 5 | 214 | 10 | 10 | 49200 |  |  | 6 | 800 | _ | 490 | 1.32 | 3 phase 400V/50Hz | 45 | _ | _ | X |  |  |  |  | X
961 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 32.306 | 5 | 172 | 10 | 7 | 38300 |  |  | 6 | 800 | _ | 392 | 0.78 | 3 phase 400V/50Hz | 41 | _ | _ | X |  |  |  |  | X
962 | X |  |  | 5208 | 1252 | 1340 | 915 | glycol (34 %) - water | 24.0417 | 5 | 128 | 10 | 4 | 27400 |  |  | 6 | 800 | _ | 294 | 0.3 | 3 phase 400V/50Hz | 37 | _ | _ | X |  |  |  |  | X
963 | X |  |  | 2270 | 1090 | 1590 | 440 | glycol (34 %) - water | 25 | 5 | 131 | 10 | 42 | 46000 |  | 1 | 2 | 800 | _ | 910 | 3.6 | 3 phase 400V/50Hz 6P | 51 | 326 | 54 | X | X |  |  |  | X
964 | X |  |  | 2270 | 1090 | 1590 | 490 | glycol (34 %) - water | 29 | 5 | 150 | 10 | 51 | 45000 |  | 1 | 2 | 800 | _ | 910 | 3.6 | 3 phase 400V/50Hz 6P | 51 | 436 | 74 | X | X |  |  |  | X
965 | X |  |  | 3210 | 1090 | 1590 | 660 | glycol (34 %) - water | 39 | 5 | 204 | 10 | 59 | 70000 |  | 1 | 3 | 800 | _ | 910 | 5.4 | 3 phase 400V/50Hz 6P | 53 | 490 | 82 | X | X |  |  |  | X
966 | X |  |  | 3210 | 1090 | 1590 | 730 | glycol (34 %) - water | 44 | 5 | 229 | 10 | 56 | 66000 |  | 1 | 3 | 800 | _ | 910 | 5.4 | 3 phase 400V/50Hz 6P | 53 | 654 | 108 | X | X |  |  |  | X
967 | X |  |  | 4180 | 1090 | 1590 | 880 | glycol (34 %) - water | 52 | 5 | 275 | 10 | 60 | 92000 |  | 1 | 4 | 800 | _ | 910 | 7.2 | 3 phase 400V/50Hz 6P | 54 | 654 | 110 | X | X |  |  |  | X
968 | X |  |  | 4180 | 1090 | 1590 | 970 | glycol (34 %) - water | 59 | 5 | 307 | 10 | 60 | 88500 |  | 1 | 4 | 800 | _ | 910 | 7.2 | 3 phase 400V/50Hz 6P | 54 | 872 | 144 | X | X |  |  |  | X
969 | X |  |  | 5150 | 1090 | 1590 | 1100 | glycol (34 %) - water | 64 | 5 | 338 | 10 | 57 | 114000 |  | 1 | 5 | 800 | _ | 910 | 9 | 3 phase 400V/50Hz 6P | 55 | 816 | 134 | X | X |  |  |  | X
970 | X |  |  | 5150 | 1090 | 1590 | 1210 | glycol (34 %) - water | 75 | 5 | 390 | 10 | 73 | 112000 |  | 1 | 5 | 800 | _ | 910 | 9 | 3 phase 400V/50Hz 6P | 55 | 1090 | 180 | X | X |  |  |  | X
971 | X |  |  | 1610 | 780 | 1065 | 96 | glycol (34 %) - water | 9.4 | 5 | 46 | 10 | 50 | 11800 |  | 1 | 2 | 500 | _ | 1360 | 1.4 | 3 phase 400V/50Hz 4P | 51 | 96 | 15.8 | X | X |  |  |  | X
972 | X |  |  | 1610 | 780 | 1065 | 110 | glycol (34 %) - water | 10.6 | 5 | 51 | 10 | 54 | 11200 |  | 1 | 2 | 500 | _ | 1360 | 1.4 | 3 phase 400V/50Hz 4P | 51 | 128 | 21.2 | X | X |  |  |  | X
973 | X |  |  | 2265 | 780 | 1065 | 138 | glycol (34 %) - water | 14.2 | 5 | 69 | 10 | 48 | 17700 |  | 1 | 3 | 500 | _ | 1360 | 2.1 | 3 phase 400V/50Hz 4P | 53 | 144 | 23.6 | X | X |  |  |  | X
974 | X |  |  | 2265 | 780 | 1065 | 158 | glycol (34 %) - water | 16 | 5 | 77 | 10 | 58 | 16800 |  | 1 | 3 | 500 | _ | 1360 | 2.1 | 3 phase 400V/50Hz 4P | 53 | 192 | 31.6 | X | X |  |  |  | X
975 | X |  |  | 2920 | 780 | 1065 | 181 | glycol (34 %) - water | 19 | 5 | 92 | 10 | 59 | 23600 |  | 1 | 4 | 500 | _ | 1360 | 2.8 | 3 phase 400V/50Hz 4P | 54 | 192 | 31.4 | X | X |  |  |  | X
976 | X |  |  | 2920 | 780 | 1065 | 209 | glycol (34 %) - water | 21.3 | 5 | 103 | 10 | 60 | 22500 |  | 1 | 4 | 500 | _ | 1360 | 2.8 | 3 phase 400V/50Hz 4P | 54 | 256 | 42 | X | X |  |  |  | X
977 | X |  |  | 3575 | 780 | 1065 | 231 | glycol (34 %) - water | 24 | 5 | 115 | 10 | 55 | 29500 |  | 1 | 5 | 500 | _ | 1360 | 3.5 | 3 phase 400V/50Hz 4P | 55 | 240 | 39.2 | X | X |  |  |  | X
978 | X |  |  | 3575 | 780 | 1065 | 267 | glycol (34 %) - water | 26.7 | 5 | 128 | 10 | 62 | 28000 |  | 1 | 5 | 500 | _ | 1360 | 3.5 | 3 phase 400V/50Hz 4P | 55 | 320 | 52.2 | X | X |  |  |  | X
979 | X |  |  | 2100 | 800 | 950 | 135 | glycol (20 %) - water | 3.6 | 6 | 25 | 2.5 | 35 | 15000 |  | _ | 3 | 450 | _ | _ | 2.4 | 1 phase 200/270 V | 64 | _ | _ | X |  | X |  | X |  |  | 5000 |  |  |  |  | 5000
980 | X |  |  | 2400 | 1050 | 950 | 165 | glycol (20 %) - water | 3.6 | 6 | 35 | 2.5 | 35 | 20000 |  |  | 3 | 630 | _ | _ | 0.9 | 2 phase 200/270 V | 67 | _ | _ | X |  | X |  | X
981 |  |  | X | 914 | 1207 | 2036 | 405 | Water | _ | _ | 35.17 | _ | _ | 6440 |  |  | 1 | _ | _ | _ | 0.75 | 3 phase 400V/50Hz | _ | _ | _
982 |  |  | X | 914 | 1207 | 2036 | 410 | Water | _ | _ | 52.75 | _ | _ | 6984 |  |  | 1 | _ | _ | _ | 1.1 | 3 phase 400V/50Hz | _ | _ | _
983 |  |  | X | 914 | 1207 | 2036 | 425 | Water | _ | _ | 70.34 | _ | _ | 7884 |  |  | 1 | _ | _ | _ | 1.5 | 3 phase 400V/50Hz | _ | _ | _
984 |  |  | X | 914 | 1207 | 2036 | 435 | Water | _ | _ | 87.92 | _ | _ | 9000 |  |  | 1 | _ | _ | _ | 2.2 | 3 phase 400V/50Hz | _ | _ | _
985 |  |  | X | 1829 | 1207 | 2036 | 655 | Water | _ | _ | 105.51 | _ | _ | 13464 |  |  | 1 | _ | _ | _ | 1.5 | 3 phase 400V/50Hz | _ | _ | _
986 |  |  | X | 1829 | 1207 | 2036 | 685 | Water | _ | _ | 140.67 | _ | _ | 16128 |  |  | 1 | _ | _ | _ | 2.2 | 3 phase 400V/50Hz | _ | _ | _
987 |  |  | X | 1829 | 1207 | 2036 | 695 | Water | _ | _ | 158.26 | _ | _ | 17892 |  |  | 1 | _ | _ | _ | 4 | 3 phase 400V/50Hz | _ | _ | _
988 |  |  | X | 1829 | 1207 | 2506 | 780 | Water | _ | _ | 193.43 | _ | _ | 18576 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 400V/50Hz | _ | _ | _
989 |  |  | X | 2737 | 1207 | 2036 | 1050 | Water | _ | _ | 228.6 | _ | _ | 25992 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 400V/50Hz | _ | _ | _
990 |  |  | X | 2737 | 1207 | 2220 | 1075 | Water | _ | _ | 246.18 | _ | _ | 29232 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 400V/50Hz | _ | _ | _
991 |  |  | X | 2737 | 1207 | 2506 | 1135 | Water | _ | _ | 263.76 | _ | _ | 28872 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 400V/50Hz | _ | _ | _
992 |  |  | X | 2737 | 1207 | 2506 | 1140 | Water | _ | _ | 298.93 | _ | _ | 31788 |  |  | 1 | _ | _ | _ | 7.5 | 3 phase 400V/50Hz | _ | _ | _
993 |  |  | X | 3658 | 1207 | 2036 | 1255 | Water | _ | _ | 334.1 | _ | _ | 39744 |  |  | 1 | _ | _ | _ | 7.5 | 3 phase 400V/50Hz | _ | _ | _
994 |  |  | X | 3658 | 1207 | 2675 | 1445 | Water | _ | _ | 369.27 | _ | _ | 39240 |  |  | 1 | _ | _ | _ | 7.5 | 3 phase 400V/50Hz | _ | _ | _
995 |  |  | X | 3658 | 1207 | 2675 | 1475 | Water | _ | _ | 422.02 | _ | _ | 45288 |  |  | 1 | _ | _ | _ | 11 | 3 phase 400V/50Hz | _ | _ | _
996 |  |  | X | 3658 | 1207 | 3350 | 1665 | Water | _ | _ | 474.78 | _ | _ | 44856 |  |  | 1 | _ | _ | _ | 11 | 3 phase 400V/50Hz | _ | _ | _
997 |  |  | X | 4240 | 4970 | 7330 | 14932.06 | Water | 397.24 | 6.95 | 3210.2 | 5.77 | 33.8 | 253152 | 7000 |  | 1 | _ | _ | _ | 18.64 | _ | _ | _ | _ | [7 empty] | 60000 |  |  |  |  | 60000
998 |  |  | X | 800 | 800 | 2110 | 75 | Water | 7.1 | 6 | 49.53 | _ | 42 | 4300 |  |  | 1 | _ | _ | _ | 0.55 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 52 | _ | _
999 |  |  | X | 800 | 800 | 2110 | 75 | Water | 9.9 | 6 | 69.06 | _ | 32 | 7100 |  |  | 1 | _ | _ | _ | 0.75 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 52 | _ | _
1000 |  |  | X | 1000 | 1000 | 2595 | 85 | Water | 12.7 | 6 | 88.6 | _ | 52 | 7100 |  |  | 1 | _ | _ | _ | 0.75 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 54 | _ | _
1001 |  |  | X | 1000 | 1000 | 2595 | 95 | Water | 15.4 | 6 | 107.44 | _ | 32 | 7100 |  |  | 1 | _ | _ | _ | 0.75 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 54 | _ | _
1002 |  |  | X | 1000 | 1000 | 2595 | 95 | Water | 18 | 6 | 125.58 | _ | 42 | 12000 |  |  | 1 | _ | _ | _ | 1.1 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 54 | _ | _
1003 |  |  | X | 1200 | 1200 | 2800 | 170 | Water | 24.1 | 6 | 168.14 | _ | 28 | 12000 |  |  | 1 | _ | _ | _ | 1.1 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 54 | _ | _
1004 |  |  | X | 1200 | 1200 | 2800 | 170 | Water | 28.33 | 6 | 197.67 | _ | 35 | 17000 |  |  | 1 | _ | _ | _ | 1.5 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 54 | _ | _
1005 |  |  | X | 1400 | 1400 | 2860 | 210 | Water | 34.7 | 6 | 242.09 | _ | 23 | 17000 |  |  | 1 | _ | _ | _ | 1.5 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 55 | _ | _
1006 |  |  | X | 1400 | 1400 | 2860 | 210 | Water | 43.3 | 6 | 302.33 | _ | 40 | 26000 |  |  | 1 | _ | _ | _ | 2.2 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 55 | _ | _
1007 |  |  | X | 1740 | 1740 | 3140 | 410 | Water | 58.1 | 6 | 405.35 | _ | 28 | 26000 |  |  | 1 | _ | _ | _ | 2.2 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 57 | _ | _
1008 |  |  | X | 1740 | 1740 | 3140 | 410 | Water | 70 | 6 | 488.37 | _ | 40 | 36000 |  |  | 1 | _ | _ | _ | 4 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 57 | _ | _
1009 |  |  | X | 1900 | 2100 | 3380 | 500 | Water | 82.3 | 6 | 574.19 | _ | 55 | 45000 |  |  | 1 | _ | _ | _ | 4 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 58 | _ | _
1010 |  |  | X | 2100 | 2300 | 3450 | 555 | Water | 86.7 | 6 | 604.88 | _ | 30 | 45000 |  |  | 1 | _ | _ | _ | 4 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 61 | _ | _
1011 |  |  | X | 2100 | 2300 | 3450 | 580 | Water | 110 | 6 | 767.44 | _ | 48 | 59000 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 61 | _ | _
1012 |  |  | X | 2025 | 2360 | 3685 | 850 | Water | 122.8 | 6 | 856.74 | _ | 49 | 59000 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 62 | _ | _
1013 |  |  | X | 2025 | 2360 | 3685 | 815 | Water | 135 | 6 | 941.86 | _ | 25 | 59000 |  |  | 1 | _ | _ | _ | 5.5 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 62 | _ | _
1014 |  |  | X | 2360 | 2380 | 3685 | 915 | Water | 155.5 | 6 | 1084.88 | _ | 32 | 70000 |  |  | 1 | _ | _ | _ | 7.5 | 3 phase 230 V/50 Hz or 3N 400V/50 Hz 4 poli | 64 | _ | _
1015 |  |  | X | 1988 | 3912 | 3105 | 3578 | Water |  |  | 444 | _ | [6 empty] | _ | _ | 1.5 | _ | 63 (at 1,5 m) | _ | _
1016 |  |  | X | 930 | 930 | 1570 | 167 | Water | 7.8 | 5 | 35.17 | _ | _ | 5100 |  |  | 1 | 500 | _ | _ | 0.55927 | _ | 56 (at 2 m) | _ | _
1017 |  |  | X | 1220 | 1220 | 1580 | 284 | Water | 11.7 | 5 | 52.75 | _ | _ | 8400 |  |  | 1 | 605 | _ | _ | 0.37285 | _ | 63 (at 2 m) | _ | _
1018 |  |  | X | 1220 | 1220 | 1760 | 297 | Water | 15.6 | 5 | 70.34 | _ | _ | 8400 |  |  | 1 | 605 | _ | _ | 0.37285 | _ | 63 (at 2 m) | _ | _
1019 |  |  | X | 1220 | 1220 | 1760 | 320 | Water | 19.5 | 5 | 87.92 | _ | _ | 11100 |  |  | 1 | 605 | _ | _ | 0.37285 | _ | 67 (at 2 m) | _ | _
1020 |  |  | X | 1650 | 1650 | 1720 | 500 | Water | 23.4 | 5 | 105.51 | _ | _ | 13500 |  |  | 1 | 860 | _ | _ | 0.55927 | _ | 67 (at 2 m) | _ | _
1021 |  |  | X | 1760 | 1760 | 1860 | 580 | Water | 31.2 | 5 | 140.67 | _ | _ | 16800 |  |  | 1 | 960 | _ | _ | 0.7457 | _ | 68 (at 2 m) | _ | _
1022 |  |  | X | 1980 | 1980 | 1910 | 630 | Water | 39 | 5 | 175.84 | _ | _ | 19800 |  |  | 1 | 960 | _ | _ | 0.7457 | _ | 68 (at 2 m) | _ | _
1023 |  |  | X | 1980 | 1980 | 1910 | 650 | Water | 46.8 | 5 | 211.01 | _ | _ | 25200 |  |  | 1 | 960 | _ | _ | 1.1185 | _ | 68 (at 2 m) | _ | _
1024 |  |  | X | 2160 | 2160 | 2000 | 680 | Water | 54.6 | 5 | 246.18 | _ | _ | 30600 |  |  | 1 | 1160 | _ | _ | 1.1185 | _ | 72 (at 2 m) | _ | _
1025 |  |  | X | 2160 | 2160 | 2000 | 700 | Water | 62.4 | 5 | 281.35 | _ | _ | 33000 |  |  | 1 | 1160 | _ | _ | 1.1185 | _ | 73 (at 2 m) | _ | _
1026 |  |  | X | 2660 | 2660 | 2100 | 1110 | Water | 78 | 5 | 351.69 | _ | _ | 42000 |  |  | 1 | 1500 | _ | _ | 1.4914 | _ | 68 (at 2 m) | _ | _
1027 |  |  | X | 2660 | 2660 | 2100 | 1300 | Water | 100.5 | 5 | 439.61 | _ | _ | 49800 |  |  | 1 | 1500 | _ | _ | 1.4914 | _ | 71 (at 2 m) | _ | _
1028 |  |  | X | 3420 | 3420 | 2450 | 1800 | Water | 117 | 5 | 527.53 | _ | _ | 57000 |  |  | 1 | 1700 | _ | _ | 2.2371 | _ | 71 (at 2 m) | _ | _
1029 |  |  | X | 3420 | 3420 | 2450 | 2300 | Water | 136.5 | 5 | 615.45 | _ | _ | 69000 |  |  | 1 | 1700 | _ | _ | 3.7285 | _ | 75 (at 2 m) | _ | _
1030 |  |  | X | 3940 | 3940 | 2900 | 2900 | Water | 156 | 5 | 703.37 | _ | _ | 75000 |  |  | 1 | 2100 | _ | _ | 3.7285 | _ | 73 (at 2 m) | _ | _
1031 |  |  | X | 3940 | 3940 | 2900 | 3200 | Water | 175.5 | 5 | 791.29 | _ | _ | 105000 |  |  | 1 | 2100 | _ | _ | 5.5928 | _ | 71 (at 2 m) | _ | _
1032 |  |  | X | 3940 | 3940 | 2900 | 3500 | Water | 195 | 5 | 879.21 | _ | _ | 111000 |  |  | 1 | 2100 | _ | _ | 5.5928 | _ | 71 (at 2 m) | _ | _
1033 |  |  | X | 4640 | 4640 | 3750 | 4400 | Water | 234 | 5 | 1055.06 | _ | _ | 132000 |  |  | 1 | 2400 | _ | _ | 7.457 | _ | 72 (at 2 m) | _ | _
1034 |  |  | X | 4640 | 4640 | 3750 | 4500 | Water | 273 | 5 | 1230.9 | _ | _ | 138000 |  |  | 1 | 2400 | _ | _ | 7.457 | _ | 72 (at 2 m) | _ | _
1035 |  |  | X | 5200 | 5200 | 4595 | 6700 | Water | 312 | 5 | 1406.74 | _ | _ | 156000 |  |  | 1 | 3100 | _ | _ | 11.1855 | _ | 74 (at 2 m) | _ | _
1036 |  |  | X | 5200 | 5200 | 4595 | 7000 | Water | 390 | 5 | 1758.43 | _ | _ | 165000 |  |  | 1 | 3100 | _ | _ | 11.1855 | _ | 74 (at 2 m) | _ | _
1037 |  |  | X | 5500 | 5500 | 4595 | 9300 | Water | 468 | 5 | 2110.11 | _ | _ | 225000 |  |  | 1 | 3100 | _ | _ | 14.914 | _ | 72 (at 2 m) | _ | _
1038 |  |  | X | 6520 | 6520 | 4975 | 10650 | Water | 546 | 5 | 2461.8 | _ | _ | 243000 |  |  | 1 | 3400 | _ | _ | 14.914 | _ | 72 (at 2 m) | _ | _
1039 |  |  | X | 8020 | 8020 | 5150 | 12000 | Water | 624 | 5 | 2813.48 | _ | _ | 300000 |  |  | 1 | 3600 | _ | _ | 18.6425 | _ | 74 (at 2 m) | _ | _
1040 |  |  | X | 8020 | 8020 | 5150 | 12300 | Water | 780 | 5 | 3516.85 | _ | _ | 330000 |  |  | 1 | 3600 | _ | _ | 22.371 | _ | 75 (at 2 m) | _ | _
1041 |  |  | X | 8200 | 8200 | 5410 | 13200 | Water | 936 | 5 | 4396.07 | _ | _ | 390000 |  |  | 1 | 4200 | _ | _ | 29.828 | _ | 75 (at 2 m) | _ | _
1042 |  |  | X | 8200 | 8200 | 5410 | 14100 | Water | 1170 | 5 | 5275.28 | _ | _ | 522000 |  |  | 1 | 4200 | _ | _ | 37.285 | _ | 80 (at 2 m) | _ | _
1043 |  |  | X | #REF! | _ | #REF! | 113.954 | Water | 3.4091 | 5.556 | 17.58 | 5.555 | _ | 3595.9404 |  |  | 1 | #REF! | _ | _ | 0.12428 | 1 phase 110/220 60 Hz | _ | _ | _ | [7 empty] | 1065.6015 | X |  |  |  | 1153.4385
1044 |  |  | X | #REF! | _ | #REF! | 118.948 | Water | 5.2273 | 5.556 | 28.13 | 5.555 | _ | 4495.7744 |  |  | 1 | #REF! | _ | _ | 0.12428 | 1 phase 110/220 60 Hz | _ | _ | _ | [7 empty] | 1121.848 | X |  |  |  | 1209.685
1045 |  |  | X | #REF! | _ | #REF! | 201.122 | Water | 6.8182 | 5.556 | 35.17 | 5.555 | _ | 5994.9318 |  |  | 1 | #REF! | _ | _ | 0.18643 | 1 phase 110/220 60 Hz | _ | _ | _ | [7 empty] | 1403.851 | X |  |  |  | 1491.688
1046 |  |  | X | #REF! | _ | #REF! | 243.344 | Water | 10 | 5.556 | 52.75 | 5.555 | _ | 8093.4126 |  |  | 1 | #REF! | _ | _ | 0.18643 | 1 phase 110/220 60 Hz | _ | _ | _ | [7 empty] | 1668.1325 | X |  |  |  | 1755.9695
1047 |  |  | X | #REF! | _ | #REF! | 326.426 | Water | 13.1818 | 5.556 | 70.34 | 5.555 | _ | 9093.4168 |  |  | 1 | #REF! | _ | _ | 0.37285 | 1 phase 110/220 60 Hz or 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 2346.1725 | X |  |  |  | 2504.125
1048 |  |  | X | #REF! | _ | #REF! | 402.698 | Water | 16.5909 | 5.556 | 87.92 | 5.555 | _ | 11884.6 |  |  | 1 | #REF! | _ | _ | 0.55927 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 2486.4035 | X |  |  |  | 2668.2415
1049 |  |  | X | #REF! | _ | #REF! | 487.596 | Water | 20 | 5.556 | 105.51 | 5.555 | _ | 13752.18 |  |  | 1 | #REF! | _ | _ | 0.7457 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 2879.3585 | X |  |  |  | 3093.5575
1050 |  |  | X | #REF! | _ | #REF! | 514.382 | Water | 26.8182 | 5.556 | 140.67 | 5.555 | _ | 16638.44 |  |  | 1 | #REF! | _ | _ | 1.1185 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 3368.626 | X |  |  |  | 3938.796
1051 |  |  | X | #REF! | _ | #REF! | 596.102 | Water | 33.6364 | 5.556 | 175.84 | 5.555 | _ | 19524.7 |  |  | 1 | #REF! | _ | _ | 1.1185 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 3765.4335 | X |  |  |  | 4354.0955
1052 |  |  | X | #REF! | _ | #REF! | 668.288 | Water | 40.2273 | 5.556 | 211.01 | 5.555 | _ | 24957.66 |  |  | 1 | #REF! | _ | _ | 1.1185 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 4269.3405 | X |  |  |  | 5008.25
1053 |  |  | X | #REF! | _ | #REF! | 705.97 | Water | 47.0455 | 5.556 | 246.18 | 5.555 | _ | 29711.5 |  |  | 1 | #REF! | _ | _ | 1.1185 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 5009.0205 | X |  |  |  | 6428.2815
1054 |  |  | X | #REF! | _ | #REF! | 720.952 | Water | 53.8636 | 5.556 | 281.35 | 5.555 | _ | 32088.42 |  |  | 1 | #REF! | _ | _ | 1.4914 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 5387.336 | X |  |  |  | 6854.368
1055 |  |  | X | #REF! | _ | #REF! | 1071.894 | Water | 67.0455 | 5.556 | 351.69 | 5.555 | _ | 41596.1 |  |  | 1 | #REF! | _ | _ | 2.2371 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 6177.0985 | X |  |  |  | 7939.232
1056 |  |  | X | #REF! | _ | #REF! | 1354.282 | Water | 83.8636 | 5.556 | 439.61 | 5.555 |  | 49338.068 |  |  | 1 | #REF! | _ | _ | 2.2371 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 7831.362 | X |  |  |  | 9795.3665
1057 |  |  | X | #REF! | _ | #REF! | 2601.874 | Water | 101.3636 | 5.556 | 527.53 | 5.555 |  | 56468.828 |  |  | 1 | #REF! | _ | _ | 3.7285 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 8796.028 | X |  |  |  | 12007.472
1058 |  |  | X | #REF! | _ | #REF! | 2672.698 | Water | 117.7273 | 5.556 | 615.45 | 5.555 |  | 68336.45 |  |  | 1 | #REF! | _ | _ | 3.7285 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 10879.46 | X |  |  |  | 14090.904
1059 |  |  | X | #REF! | _ | #REF! | 3455.848 | Water | 134.5455 | 5.556 | 703.37 | 5.555 |  | 74295.728 |  |  | 1 | #REF! | _ | _ | 3.7285 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 12139.998 | X |  |  |  | 15944.727
1060 |  |  | X | #REF! | _ | #REF! | 3515.776 | Water | 149.0909 | 5.556 | 791.29 | 5.555 |  | 104024.206 |  |  | 1 | #REF! | _ | _ | 5.5928 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 14268.8895 | X |  |  |  | 18548.2465
1061 |  |  | X | #REF! | _ | #REF! | 3565.716 | Water | 167.5 | 5.556 | 879.21 | 5.555 |  | 104024.206 |  |  | 1 | #REF! | _ | _ | 5.5928 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 15163.44 | X |  |  |  | 19526.011
1062 |  |  | X | #REF! | _ | #REF! | 4537.73 | Water | 200.6818 | 5.556 | 1055.06 | 5.555 |  | 130764.556 |  |  | 1 | #REF! | _ | _ | 7.457 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 18122.16 | X |  |  |  | 23511.037
1063 |  |  | X | #REF! | _ | #REF! | 4614.456 | Water | 235.4545 | 5.556 | 1230.9 | 5.555 |  | 130764.556 |  |  | 1 | #REF! | _ | _ | 7.457 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 19705.5375 | X |  |  |  | 25213.0715
1064 |  |  | X | #REF! | _ | #REF! | 6802.736 | Water | 270.4545 | 5.556 | 1406.74 | 5.555 |  | 154550.734 |  |  | 1 | #REF! | _ | _ | 11.1855 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 25585.9935 | X |  |  |  | 34570.794
1065 |  |  | X | #REF! | _ | #REF! | 7059.7 | Water | 342.0455 | 5.556 | 1758.43 | 5.555 |  | 154550.734 |  |  | 1 | #REF! | _ | _ | 11.1855 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 28542.402 | X |  |  |  | 38085.815
1066 |  |  | X | #REF! | _ | #REF! | 10731.198 | Water | 403.8636 | 5.556 | 2110.11 | 5.555 |  | 212225 |  |  | 1 | #REF! | _ | _ | 14.914 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 36367.6 | X |  |  |  | 50563.292
1067 |  |  | X | #REF! | _ | #REF! | 10953.658 | Water | 477.5 | 5.556 | 2461.8 | 5.555 |  | 212225 |  |  | 1 | #REF! | _ | _ | 14.914 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 38139.75 | X |  |  |  | 52335.442
1068 |  |  | X | #REF! | _ | #REF! | 11920.224 | Water | 515.9091 | 5.556 | 2813.48 | 5.555 |  | 297115 |  |  | 1 | #REF! | _ | _ | 22.371 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 47855.755 | X |  |  |  | 65268.2845
1069 |  |  | X | #REF! | _ | #REF! | 12420.986 | Water | 684.3182 | 5.556 | 3516.85 | 5.555 |  | 297115 |  |  | 1 | #REF! | _ | _ | 22.371 | 3 phase 220/440 60 Hz | _ | _ | _ | [7 empty] | 50074.795 | X |  |  |  | 67487.3245
1070 |  |  | X | #REF! | _ | #REF! | 64.922 | Water | 2.0455 | 5.556 | 10.6 | 5.555 |  | 1618.0034 |  |  | 1 | #REF! |  | 1200 | 0.12428 | 1 phase 115/230 60 Hz | 57 (at 2 m) | _ | _ | [7 empty] | _ |  |  |  |  | _
1071 |  |  | X | #REF! | _ | #REF! | 100.334 | Water | 3.4091 | 5.556 | 17.6 | 5.555 |  | 3599.336 |  |  | 1 | #REF! |  | 1200 | 0.12428 | 1 phase 115/230 60 Hz | 57 (at 2 m) | _ | _ | [7 empty] | 1290.5875 |  |  |  |  | 1290.5875
1072 |  |  | X | #REF! | _ | #REF! | 138.016 | Water | 5.4545 | 5.556 | 28.1 | 5.555 |  | 4499.17 |  |  | 1 | #REF! |  | 1200 | 0.12428 | 1 phase 115/230 60 Hz | 58 (at 2 m) | _ | _ | [7 empty] | 1557.1805 |  |  |  |  | 1557.1805
1073 |  |  | X | #REF! | _ | #REF! | 177.968 | Water | 6.8182 | 5.556 | 35.2 | 5.555 |  | 5993.234 |  |  | 1 | #REF! |  | 1200 | 0.18643 | 1 phase 115/230 60 Hz | 61 (at 2 m) | _ | _ | [7 empty] | 1718.9855 |  |  |  |  | 1718.9855
1074 |  |  | X | #REF! | _ | #REF! | 260.142 | Water | 10.2273 | 5.556 | 52.8 | 5.555 |  | 8404.11 |  |  | 1 | #REF! |  | 1200 | 0.37285 | 1 phase 115/230 60 Hz or 3 phase 230/460 | 61 (at 2 m) | _ | _ | [7 empty] | 2022.5625 |  |  |  |  | 2022.5625
1075 |  |  | X | #REF! | _ | #REF! | 330.512 | Water | 13.6364 | 5.556 | 70.3 | 5.555 |  | 10781.03 |  |  | 1 | #REF! |  | 1200 | 0.37285 | 1 phase 115/230 60 Hz or 3 phase 230/460 | 62 (at 2 m) | _ | _ | [7 empty] | 2731.4225 |  |  |  |  | 2731.4225
1076 |  |  | X | #REF! | _ | #REF! | 420.404 | Water | 17.0455 | 5.556 | 87.9 | 5.555 |  | 11986.468 |  |  | 1 | #REF! |  | 1200 | 0.55927 | 3 phase 230/460 60 Hz | 66 (at 2 m) | _ | _ | [7 empty] | 2893.2275 |  |  |  |  | 2893.2275
1077 |  |  | X | #REF! | _ | #REF! | 500.762 | Water | 20.4545 | 5.556 | 105.5 | 5.555 |  | 13497.51 |  |  | 1 | #REF! |  | 1200 | 0.55927 | 3 phase 230/460 60 Hz | 67 (at 2 m) | _ | _ | [7 empty] | 3421.02 |  |  |  |  | 3421.02
1078 |  |  | X | #REF! | _ | #REF! | 550.702 | Water | 27.2727 | 5.556 | 140.7 | 5.555 |  | 16791.242 |  |  | 1 | #REF! |  | 1200 | 0.7457 | 3 phase 230/460 60 Hz | 74 (at 2 m) | _ | _ | [7 empty] | 4249.3075 |  |  |  |  | 4249.3075
1079 |  |  | X | #REF! | _ | #REF! | 700.976 | Water | 37.5 | 5.556 | 175.8 | 5.555 |  | 19779.37 |  |  | 1 | #REF! |  | 1200 | 0.7457 | 3 phase 230/460 60 Hz | 74 (at 2 m) | _ | _ | [7 empty] | 4854.15 |  |  |  |  | 4854.15
1080 |  |  | X | #REF! | _ | #REF! | 750.916 | Water | 40.9091 | 5.556 | 211 | 5.555 |  | 25178.374 |  |  | 1 | #REF! |  | 1200 | 1.1185 | 3 phase 230/460 60 Hz | 75 (at 2 m) | _ | _ | [7 empty] | 5824.98 |  |  |  |  | 5824.98
1081 |  |  | X | #REF! | _ | #REF! | 961.118 | Water | 47.7273 | 5.556 | 246.2 | 5.555 |  | 30577.378 |  |  | 1 | #REF! |  | 900 | 1.1185 | 3 phase 230/460 60 Hz | 72 (at 2 m) | _ | _ | [7 empty] | 7161.7975 |  |  |  |  | 7161.7975
1082 |  |  | X | #REF! | _ | #REF! | 1041.022 | Water | 57.9545 | 5.556 | 281.3 | 5.555 |  | 32971.276 |  |  | 1 | #REF! |  | 900 | 1.1185 | 3 phase 230/460 60 Hz | 72 (at 2 m) | _ | _ | [7 empty] | 7743.525 |  |  |  |  | 7743.525
1083 |  |  | X | #REF! | _ | #REF! | 1261.212 | Water | 75 | 5.556 | 351.7 | 5.555 |  | 41969.616 |  |  | 1 | #REF! |  | 900 | 1.4914 | 3 phase 230/460 60 Hz | 76 (at 2 m) | _ | _ | [7 empty] | 9546.495 |  |  |  |  | 9546.495
1084 |  |  | X | #REF! | _ | #REF! | 1621.688 | Water | 85.2273 | 5.556 | 439.6 | 5.555 |  | 49762.518 |  |  | 1 | #REF! |  | 900 | 2.2371 | 3 phase 230/460 60 Hz | 76 (at 2 m) | _ | _ | [7 empty] | 11981.275 |  |  |  |  | 11981.275
1085 |  |  | X | #REF! | _ | #REF! | 2723.092 | Water | 109.0909 | 5.556 | 527.5 | 5.555 |  | 56961.19 |  |  | 1 | #REF! |  | 720 | 2.2371 | 3 phase 230/460 60 Hz | 75 (at 2 m) | _ | _ | [7 empty] | 15217.375 |  |  |  |  | 15217.375
1086 |  |  | X | #REF! | _ | #REF! | 2903.33 | Water | 122.7273 | 5.556 | 615.4 | 5.555 |  | 68930.68 |  |  | 1 | #REF! |  | 720 | 2.2371 | 3 phase 230/460 60 Hz | 70 (at 2 m) | _ | _ | [7 empty] | 16488.7 |  |  |  |  | 16488.7
1087 |  |  | X | #REF! | _ | #REF! | 3333.722 | Water | 145.4545 | 5.556 | 703.4 | 5.555 |  | 74940.892 |  |  | 1 | #REF! |  | 1750 | 5.5928 | 3 phase 230/460 60 Hz | 72 (at 2 m) | _ | _ | [7 empty] | 19786.44 |  |  |  |  | 19786.44
1088 |  |  | X | #REF! | _ | #REF! | 3403.638 | Water | 156.8182 | 5.556 | 791.3 | 5.555 |  | 104907.062 |  |  | 1 | #REF! |  | 1750 | 5.5928 | 3 phase 230/460 60 Hz | 72 (at 2 m) | _ | _ | [7 empty] | 22344.5 |  |  |  |  | 22344.5
1089 |  |  | X | #REF! | _ | #REF! | 3503.972 | Water | 181.8182 | 5.556 | 879.2 | 5.555 |  | 110900.296 |  |  | 1 | #REF! |  | 1750 | 5.5928 | 3 phase 230/460 60 Hz | 74 (at 2 m) | _ | _ | [7 empty] | 23423.2 |  |  |  |  | 23423.2
1090 |  |  | X | #REF! | _ | #REF! | 4004.28 | Water | 221.5909 | 5.556 | 1055.1 | 5.555 |  | 131902.082 |  |  | 1 | #REF! |  | 1750 | 7.457 | 3 phase 230/460 60 Hz | 73 (at 2 m) | _ | _ | [7 empty] | 28123.25 |  |  |  |  | 28123.25
1091 |  |  | X | #REF! | _ | #REF! | 4354.768 | Water | 255.6818 | 5.556 | 1230.9 | 5.555 |  | 137878.338 |  |  | 1 | #REF! |  | 1750 | 7.457 | 3 phase 230/460 60 Hz | 73 (at 2 m) | _ | _ | [7 empty] | 30434.75 |  |  |  |  | 30434.75
1092 |  |  | X | #REF! | _ | #REF! | 7107.824 | Water | 306.8182 | 5.556 | 1406.7 | 5.555 |  | 155875.018 |  |  | 1 | #REF! |  | 1750 | 11.1855 | 3 phase 230/460 60 Hz | _ | _ | _ | [7 empty] | _ |  |  |  |  | _
1093 |  |  | X | #REF! | _ | #REF! | 7668.06 | Water | 375 | 5.556 | 1758.4 | 5.555 |  | 164856.38 |  |  | 1 | #REF! |  | 1750 | 11.1855 | 3 phase 230/460 60 Hz | _ | _ | _ | [7 empty] | _ |  |  |  |  | _
1094 |  |  | X | #REF! | _ | #REF! | 9930.796 | Water | 454.5455 | 5.556 | 2110.1 | 5.555 |  | 224805.698 |  |  | 1 | #REF! |  | 1750 | 14.914 | 3 phase 230/460 60 Hz | _ | _ | _ | [7 empty] | _ |  |  |  |  | _
1095 |  |  | X | #REF! | _ | #REF! | 11662.352 | Water | 522.7273 | 5.556 | 2461.8 | 5.555 |  | 233804.038 |  |  | 1 | #REF! |  | 1750 | 14.914 | 3 phase 230/460 60 Hz | _ | _ | _ | [7 empty] | _ |  |  |  |  | _
1096 |  |  | X | #REF! | _ | #REF! | 12012.84 | Water | 602.2727 | 5.556 | 2813.5 | 5.555 |  | 299746.59 |  |  | 1 | _ |  | _ | 18.6425 | 3 phase 230/460 60 Hz | _ | _ | _ | [7 empty] | _ |  |  |  |  | _
1097 |  |  | X | #REF! | _ | #REF! | 12313.388 | Water | 681.8182 | 5.556 | 3516.9 | 5.555 |  | 311733.058 |  |  | 1 | _ |  | _ | 22.371 | 3 phase 230/460 60 Hz | _ | _ | _ | [7 empty] | _ |  |  |  |  | _
1098 |  |  | X | _ | _ | _ | 799.04 | Water | 22.5 | 5.556 | 116.1 | 3.88 |  | 16298.88 |  |  | 1 |  |  |  | 1.4914 |  |  | _ | _ | [12 empty] | _
1099 |  |  | X | _ | _ | _ | 835.36 | Water | 25.2273 | 5.556 | 130.1 | 3.88 |  | 16129.1 |  |  | 1 |  |  |  | 1.4914 |  |  | _ | [13 empty] | _
1100 |  |  | X | _ | _ | _ | 821.74 | Water | 26.5909 | 5.556 | 137.2 | 3.88 |  | 18506.02 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1101 |  |  | X | _ | _ | _ | 858.06 | Water | 29.3182 | 5.556 | 151.2 | 3.88 |  | 18166.46 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1102 |  |  | X | _ | _ | _ | 1116.84 | Water | 38.8636 | 5.556 | 200.5 | 3.88 |  | 25976.34 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1103 |  |  | X | _ | _ | _ | 1162.24 | Water | 43.6364 | 5.556 | 225.1 | 3.88 |  | 25636.78 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1104 |  |  | X | _ | _ | _ | 1125.92 | Water | 45.6818 | 5.556 | 235.6 | 3.88 |  | 30560.4 |  |  | 1 |  |  |  | 3.7285 |  |  | _ | [13 empty] | _
1105 |  |  | X | _ | _ | _ | 1171.32 | Water | 50.4545 | 5.556 | 260.2 | 3.88 |  | 30051.06 |  |  | 1 |  |  |  | 3.7285 |  |  | _ | [13 empty] | _
1106 |  |  | X | _ | _ | _ | 1634.4 | Water | 51.8182 | 5.556 | 267.3 | 3.88 |  | 35993.36 |  |  | 2 |  |  |  | 2.9828 |  |  | _ | [13 empty] | _
1107 |  |  | X | _ | _ | _ | 1707.04 | Water | 58.6364 | 5.556 | 302.4 | 3.88 |  | 35314.24 |  |  | 2 |  |  |  | 2.9828 |  |  | _ | [13 empty] | _
1108 |  |  | X | _ | _ | _ | 1679.8 | Water | 61.3636 | 5.556 | 316.5 | 3.88 |  | 40916.98 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1109 |  |  | X | _ | _ | _ | 1752.44 | Water | 68.1818 | 5.556 | 351.7 | 3.88 |  | 40068.08 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1110 |  |  | X | _ | _ | _ | 2133.8 | Water | 78.4091 | 5.556 | 404.4 | 3.88 |  | 52631.8 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1111 |  |  | X | _ | _ | _ | 2224.6 | Water | 87.9545 | 5.556 | 453.7 | 3.88 |  | 51613.12 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1112 |  |  | X | _ | _ | _ | 2151.96 | Water | 93.4091 | 5.556 | 481.8 | 3.88 |  | 61799.92 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1113 |  |  | X | _ | _ | _ | 2242.76 | Water | 102.2727 | 5.556 | 527.5 | 3.88 |  | 60611.46 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1114 |  |  | X | _ | _ | _ | 2315.4 | Water | 60.6818 | 5.556 | 393.89 | 3.88 |  | 44991.7 |  |  | 1 |  |  |  | 3.7285 |  |  | _ | [13 empty] | 8146
1115 |  |  | X | _ | _ | _ | 2424.36 | Water | 94.0909 | 5.556 | 485.33 | 3.88 |  | 50424.66 |  |  | 1 | [6 empty] | 5.5928 | [13 empty] | 8438
1116 |  |  | X | _ | _ | _ | 4612.64 | Water | 122.0455 | 5.556 | 629.5 | 3.88 |  | 76740.56 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1117 |  |  | X | _ | _ | _ | 4630.8 | Water | 153.4091 | 5.556 | 791.3 | 3.88 |  | 90153.18 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1118 |  |  | X | _ | _ | _ | 4667.12 | Water | 168.4091 | 5.556 | 868.7 | 3.88 |  | 102716.9 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1119 |  |  | X | _ | _ | _ | 4812.4 | Water | 170.4545 | 5.556 | 879.2 | 3.88 |  | 88794.94 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1120 |  |  | X | _ | _ | _ | 4848.72 | Water | 188.8636 | 5.556 | 974.2 | 3.88 |  | 100849.32 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1121 |  |  | X | _ | _ | _ | 4875.96 | Water | 205.9091 | 5.556 | 1062.1 | 3.88 |  | 110526.78 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1122 |  |  | X | _ | _ | _ | 5075.72 | Water | 214.7727 | 5.556 | 1107.8 | 3.88 |  | 108659.2 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1123 |  |  | X | _ | _ | _ | 5139.28 | Water | 234.5455 | 5.556 | 1209.8 | 3.88 |  | 123599.84 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1124 |  |  | X | _ | _ | _ | 5311.8 | Water | 147.9545 | 5.556 | 763.2 | 3.88 |  | 90322.96 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1125 |  |  | X | _ | _ | _ | 5329.96 | Water | 186.8182 | 5.556 | 963.6 | 3.88 |  | 106282.28 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1126 |  |  | X | _ | _ | _ | 5366.28 | Water | 202.5 | 5.556 | 1044.5 | 3.88 |  | 121222.92 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1127 |  |  | X | _ | _ | _ | 5393.52 | Water | 217.5 | 5.556 | 1121.9 | 3.88 |  | 132937.74 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1128 |  |  | X | _ | _ | _ | 5538.8 | Water | 207.2727 | 5.556 | 1069.1 | 3.88 |  | 104584.48 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1129 |  |  | X | _ | _ | _ | 5575.12 | Water | 225.6818 | 5.556 | 1164.1 | 3.88 |  | 119185.56 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1130 |  |  | X | _ | _ | _ | 5602.36 | Water | 244.0909 | 5.556 | 1259 | 3.88 |  | 130560.82 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1131 |  |  | X | _ | _ | _ | 5820.28 | Water | 235.9091 | 5.556 | 1216.8 | 3.88 |  | 117317.98 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1132 |  |  | X | _ | _ | _ | 5847.52 | Water | 254.3182 | 5.556 | 1311.8 | 3.88 |  | 128523.46 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1133 |  |  | X | _ | _ | _ | 5656.84 | Water | 267.9545 | 5.556 | 1382.1 | 3.88 |  | 148557.5 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1134 |  |  | X | _ | _ | _ | 5902 | Water | 282.2727 | 5.556 | 1456 | 3.88 |  | 146010.8 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1135 |  |  | X | _ | _ | _ | 4612.64 | Water | 122.0455 | 5.556 | 629.5 | 3.88 |  | 76740.56 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1136 |  |  | X | _ | _ | _ | 4630.8 | Water | 153.4091 | 5.556 | 791.3 | 3.88 |  | 90153.18 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1137 |  |  | X | _ | _ | _ | 4667.12 | Water | 168.4091 | 5.556 | 868.7 | 3.88 |  | 102716.9 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1138 |  |  | X | _ | _ | _ | 4812.4 | Water | 170.4545 | 5.556 | 879.2 | 3.88 |  | 88794.94 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1139 |  |  | X | _ | _ | _ | 4848.72 | Water | 188.8636 | 5.556 | 974.2 | 3.88 |  | 100849.32 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1140 |  |  | X | _ | _ | _ | 4875.96 | Water | 205.9091 | 5.556 | 1062.1 | 3.88 |  | 110526.78 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1141 |  |  | X | _ | _ | _ | 5075.72 | Water | 214.7727 | 5.556 | 1107.8 | 3.88 |  | 108659.2 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1142 |  |  | X | _ | _ | _ | 5139.28 | Water | 234.5455 | 5.556 | 1209.8 | 3.88 |  | 123599.84 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1143 |  |  | X | _ | _ | _ | 5311.8 | Water | 147.9545 | 5.556 | 763.2 | 3.88 |  | 90322.96 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1144 |  |  | X | _ | _ | _ | 5329.96 | Water | 186.8182 | 5.556 | 963.6 | 3.88 |  | 106282.28 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1145 |  |  | X | _ | _ | _ | 5366.28 | Water | 202.5 | 5.556 | 1044.5 | 3.88 |  | 121222.92 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1146 |  |  | X | _ | _ | _ | 5393.52 | Water | 217.5 | 5.556 | 1121.9 | 3.88 |  | 132937.74 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1147 |  |  | X | _ | _ | _ | 5538.8 | Water | 207.2727 | 5.556 | 1069.1 | 3.88 |  | 104584.48 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1148 |  |  | X | _ | _ | _ | 5575.12 | Water | 225.6818 | 5.556 | 1164.1 | 3.88 |  | 119185.56 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1149 |  |  | X | _ | _ | _ | 5602.36 | Water | 244.0909 | 5.556 | 1259 | 3.88 |  | 130560.82 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1150 |  |  | X | _ | _ | _ | 5820.28 | Water | 235.9091 | 5.556 | 1216.8 | 3.88 |  | 117317.98 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1151 |  |  | X | _ | _ | _ | 5847.52 | Water | 254.3182 | 5.556 | 1311.8 | 3.88 |  | 128523.46 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1152 |  |  | X | _ | _ | _ | 5656.84 | Water | 267.9545 | 5.556 | 1382.1 | 3.88 |  | 148557.5 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1153 |  |  | X | _ | _ | _ | 5902 | Water | 282.2727 | 5.556 | 1456 | 3.88 |  | 146010.8 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1154 |  |  | X | _ | _ | _ | 6474.04 | Water | 246.8182 | 5.556 | 1273.1 | 3.88 |  | 136163.56 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1155 |  |  | X | _ | _ | _ | 6501.28 | Water | 272.0455 | 5.556 | 1403.2 | 3.88 |  | 149066.84 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1156 |  |  | X | _ | _ | _ | 6256.12 | Water | 242.7273 | 5.556 | 1252 | 3.88 |  | 151613.54 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1157 |  |  | X | _ | _ | _ | 6319.68 | Water | 283.6364 | 5.556 | 1463 | 3.88 |  | 172326.7 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1158 |  |  | X | _ | _ | _ | 6564.84 | Water | 316.3636 | 5.556 | 1631.8 | 3.88 |  | 168931.1 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1159 |  |  | X | _ | _ | _ | 6782.76 | Water | 285 | 5.556 | 1470 | 3.88 |  | 146689.92 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1160 |  |  | X | _ | _ | _ | 6846.32 | Water | 330 | 5.556 | 1702.2 | 3.88 |  | 166214.62 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1161 |  |  | X | _ | _ | _ | 6891.72 | Water | 361.3636 | 5.556 | 1863.9 | 3.88 |  | 181834.38 |  |  | 2 |  |  |  | 29.828 |  |  | _ | [13 empty] | _
1162 |  |  | X | _ | _ | _ | 7109.64 | Water | 215.4545 | 5.556 | 1111.3 | 3.88 |  | 137012.46 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1163 |  |  | X | _ | _ | _ | 7145.96 | Water | 258.4091 | 5.556 | 1332.9 | 3.88 |  | 155858.04 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1164 |  |  | X | _ | _ | _ | 7400.2 | Water | 236.5909 | 5.556 | 1220.3 | 3.88 |  | 135144.88 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1165 |  |  | X | _ | _ | _ | 7436.52 | Water | 278.8636 | 5.556 | 1438.4 | 3.88 |  | 153650.9 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1166 |  |  | X | _ | _ | _ | 7463.76 | Water | 304.7727 | 5.556 | 1572 | 3.88 |  | 168251.98 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1167 |  |  | X | _ | _ | _ | 7236.76 | Water | 318.4091 | 5.556 | 1642 | 3.88 |  | 194567.88 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1168 |  |  | X | _ | _ | _ | 7754.32 | Water | 302.7273 | 5.556 | 1561.5 | 3.88 |  | 150934.42 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1169 |  |  | X | _ | _ | _ | 7781.56 | Water | 327.2727 | 5.556 | 1688.1 | 3.88 |  | 165365.72 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1170 |  |  | X | _ | _ | _ | 7527.32 | Water | 351.8182 | 5.556 | 1814.7 | 3.88 |  | 191002.5 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1171 |  |  | X | _ | _ | _ | 7845.12 | Water | 371.5909 | 5.556 | 1916.7 | 3.88 |  | 187776.68 |  |  | 2 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1172 |  |  | X | _ | _ | _ | 7572.72 | Water | 392.7273 | 5.556 | 2025.7 | 3.88 |  | 208829.4 |  |  | 2 |  |  |  | 29.828 |  |  | _ | [13 empty] | _
1173 |  |  | X | _ | _ | _ | 7917.76 | Water | 432.2727 | 5.556 | 2229.7 | 3.88 |  | 220204.66 |  |  | 2 |  |  |  | 37.285 |  |  | _ | [13 empty] | _
1174 |  |  | X | _ | _ | _ | 685.54 | Water | 36.72 | 5.556 | 128.37 | 3.88 |  | 15619.76 |  |  | 1 |  |  |  | 1.5 |  |  | _ | [8 empty] | 3452 |  |  |  |  | 3452
1175 |  |  | X | _ | _ | _ | 758.18 | Water | 18.36 | 5.556 | 147.71 | 3.88 | 17.9 | 15110.42 |  |  | 1 |  |  |  | 1.5 |  |  | _ | [8 empty] | 3190 |  |  |  |  | 3190
1176 |  |  | X | _ | _ | _ | 1044.2 | Water | 22.7273 | 5.556 | 145.8914 | 3.88 | 4.1 | 15449.98 |  |  | 2 |  |  |  | 2.9828 |  |  | _ | [13 empty] | _
1177 |  |  | X | _ | _ | _ | 1057.82 | Water | 26.3636 | 5.556 | 169.234 | 3.88 |  | 17487.34 |  |  | 2 |  |  |  | 4.4742 |  |  | _ | [13 empty] | _
1178 |  |  | X | _ | _ | _ | 1062.36 | Water | 32.0455 | 5.556 | 205.7069 | 3.88 |  | 20543.38 |  |  | 2 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1179 |  |  | X | _ | _ | _ | 1085.06 | Water | 37.2727 | 5.556 | 239.2619 | 3.88 |  | 23259.86 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1180 |  |  | X | _ | _ | _ | 1116.84 | Water | 41.3636 | 5.556 | 265.5224 | 3.88 |  | 22580.74 |  |  | 2 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1181 |  |  | X | _ | _ | _ | 1121.38 | Water | 45.4545 | 5.556 | 291.7828 | 3.88 |  | 24618.1 |  |  | 2 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1182 |  |  | X | _ | _ | _ | 1493.66 | Water | 48.4091 | 5.556 | 310.7487 | 3.88 |  | 31069.74 |  |  | 3 |  |  |  | 16.7782 |  |  | _ | [13 empty] | _
1183 |  |  | X | _ | _ | _ | 1498.2 | Water | 53.8636 | 5.556 | 345.7627 | 3.88 |  | 33786.22 |  |  | 3 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1184 |  |  | X | _ | _ | _ | 1511.82 | Water | 60 | 5.556 | 385.1533 | 3.88 |  | 32937.32 |  |  | 3 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1185 |  |  | X | _ | _ | _ | 1924.96 | Water | 65.2273 | 5.556 | 418.7084 | 3.88 |  | 41426.32 |  |  | 4 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1186 |  |  | X | _ | _ | _ | 2006.68 | Water | 73.1818 | 5.556 | 469.7704 | 3.88 |  | 40407.64 |  |  | 4 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1187 |  |  | X | _ | _ | _ | 2092.94 | Water | 77.9545 | 5.556 | 500.4076 | 3.88 |  | 39049.4 |  |  | 4 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1188 |  |  | X | _ | _ | _ | 2065.7 | Water | 84.0909 | 5.556 | 539.7982 | 3.88 |  | 45670.82 |  |  | 4 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1189 |  |  | X | _ | _ | _ | 2151.96 | Water | 88.6364 | 5.556 | 568.9765 | 3.88 |  | 44142.8 |  |  | 4 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1190 |  |  | X | _ | _ | _ | 2179.2 | Water | 96.8182 | 5.556 | 621.4974 | 3.88 |  | 48217.52 |  |  | 4 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1191 |  |  | X | _ | _ | _ | 2873.82 | Water | 109.5455 | 5.556 | 703.1966 | 3.88 |  | 68251.56 |  |  | 6 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1192 |  |  | X | _ | _ | _ | 2996.4 | Water | 122.2727 | 5.556 | 784.8958 | 3.88 |  | 66553.76 |  |  | 6 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1193 |  |  | X | _ | _ | _ | 3010.02 | Water | 131.8182 | 5.556 | 846.1702 | 3.88 |  | 71137.82 |  |  | 6 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1194 |  |  | X | _ | _ | _ | 3137.14 | Water | 138.6364 | 5.556 | 889.9376 | 3.88 |  | 68930.68 |  |  | 6 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1195 |  |  | X | _ | _ | _ | 3159.84 | Water | 146.8182 | 5.556 | 942.4586 | 3.88 |  | 72835.62 |  |  | 6 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1196 |  |  | X | _ | _ | _ | 2837.5 | Water | 106.8182 | 5.556 | 685.6897 | 3.88 |  | 65704.86 |  |  | 4 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1197 |  |  | X | _ | _ | _ | 2946.46 | Water | 119.3182 | 5.556 | 765.9299 | 3.88 |  | 63837.28 |  |  | 4 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1198 |  |  | X | _ | _ | _ | 2960.08 | Water | 128.1818 | 5.556 | 822.8276 | 3.88 |  | 68591.12 |  |  | 4 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1199 |  |  | X | _ | _ | _ | 3069.04 | Water | 134.7727 | 5.556 | 865.1361 | 3.88 |  | 67063.1 |  |  | 4 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1200 |  |  | X | _ | _ | _ | 3091.74 | Water | 142.5 | 5.556 | 914.7392 | 3.88 |  | 70968.04 |  |  | 4 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1201 |  |  | X | _ | _ | _ | 4158.64 | Water | 150.6818 | 5.556 | 967.2601 | 3.88 |  | 93548.78 |  |  | 6 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1202 |  |  | X | _ | _ | _ | 4181.34 | Water | 160.9091 | 5.556 | 1032.9112 | 3.88 |  | 99151.52 |  |  | 6 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1203 |  |  | X | _ | _ | _ | 4253.98 | Water | 178.6364 | 5.556 | 1146.7065 | 3.88 |  | 108659.2 |  |  | 6 |  |  |  | 29.828 |  |  | _ | [13 empty] | _
1204 |  |  | X | _ | _ | _ | 4340.24 | Water | 179.3182 | 5.556 | 1151.0833 | 3.88 |  | 96435.04 |  |  | 6 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1205 |  |  | X | _ | _ | _ | 4412.88 | Water | 197.2727 | 5.556 | 1266.3375 | 3.88 |  | 105603.16 |  |  | 6 |  |  |  | 29.828 |  |  | _ | [13 empty] | _
1206 |  |  | X | _ | _ | _ | 4571.78 | Water | 207.2727 | 5.556 | 1330.5297 | 3.88 |  | 103226.24 |  |  | 6 |  |  |  | 29.828 |  |  | _ | [13 empty] | _
1207 |  |  | X | _ | _ | _ | 4576.32 | Water | 222.2727 | 5.556 | 1426.8181 | 3.88 |  | 107300.96 |  |  | 6 |  |  |  | 37.285 |  |  | _ | [13 empty] | _
1208 |  |  | X | _ | _ | _ | 1130.46 | Water | 18.4091 | 5.556 | 118.172 | 3.88 |  | 11918.556 |  |  | 1 |  |  |  | 1.1185 |  |  | _ | [13 empty] | _
1209 |  |  | X | _ | _ | _ | 1130.46 | Water | 22.9545 | 5.556 | 147.3503 | 3.88 |  | 15025.53 |  |  | 1 |  |  |  | 1.4914 |  |  | _ | [13 empty] | _
1210 |  |  | X | _ | _ | _ | 1139.54 | Water | 26.1364 | 5.556 | 167.7751 | 3.88 |  | 17198.714 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1211 |  |  | X | _ | _ | _ | 1175.86 | Water | 29.0909 | 5.556 | 186.741 | 3.88 |  | 16876.132 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1212 |  |  | X | _ | _ | _ | 1180.4 | Water | 33.8636 | 5.556 | 217.3782 | 3.88 |  | 20000.084 |  |  | 1 |  |  |  | 3.7285 |  |  | _ | [13 empty] | _
1213 |  |  | X | _ | _ | _ | 1198.56 | Water | 38.1818 | 5.556 | 245.0976 | 3.88 |  | 22903.322 |  |  | 1 |  |  |  | 5.5928 |  |  | _ | [13 empty] | _
1214 |  |  | X | _ | _ | _ | 1834.16 | Water | 39.3182 | 5.556 | 252.3922 | 3.88 |  | 25263.264 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1215 |  |  | X | _ | _ | _ | 1838.7 | Water | 46.1364 | 5.556 | 296.1596 | 3.88 |  | 29949.192 |  |  | 1 |  |  |  | 3.7285 |  |  | _ | [13 empty] | _
1216 |  |  | X | _ | _ | _ | 1902.26 | Water | 49.0909 | 5.556 | 315.1255 | 3.88 |  | 24719.968 |  |  | 1 |  |  |  | 2.2371 |  |  | _ | [13 empty] | _
1217 |  |  | X | _ | _ | _ | 1875.02 | Water | 51.1364 | 5.556 | 328.2557 | 3.88 |  | 29405.896 |  |  | 1 |  |  |  | 3.7285 |  |  | _ | [13 empty] | _
1218 |  |  | X | _ | _ | _ | 1861.4 | Water | 52.2727 | 5.556 | 335.5503 | 3.88 |  | 34312.538 |  |  | 1 |  |  |  | 5.5928 |  |  | _ | [13 empty] | _
1219 |  |  | X | _ | _ | _ | 1870.48 | Water | 56.1364 | 5.556 | 360.3518 | 3.88 |  | 33888.088 |  |  | 1 |  |  |  | 5.5928 |  |  | _ | [13 empty] | _
1220 |  |  | X | _ | _ | _ | 1911.34 | Water | 61.5909 | 5.556 | 395.3657 | 3.88 |  | 36163.14 |  |  | 1 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1221 |  |  | X | _ | _ | _ | 1924.96 | Water | 64.0909 | 5.556 | 411.4138 | 3.88 |  | 33531.55 |  |  | 1 |  |  |  | 5.5928 |  |  | _ | [13 empty] | _
1222 |  |  | X | _ | _ | _ | 1943.12 | Water | 69.5455 | 5.556 | 446.4277 | 3.88 |  | 36163.14 |  |  | 1 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1223 |  |  | X | _ | _ | _ | 2465.22 | Water | 68.6364 | 5.556 | 440.5921 | 3.88 |  | 44940.766 |  |  | 1 |  |  |  | 7.457 |  |  | _ | [13 empty] | _
1224 |  |  | X | _ | _ | _ | 2510.62 | Water | 77.9545 | 5.556 | 500.4076 | 3.88 |  | 51426.362 |  |  | 1 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1225 |  |  | X | _ | _ | _ | 2537.86 | Water | 83.8636 | 5.556 | 538.3393 | 3.88 |  | 50866.088 |  |  | 1 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1226 |  |  | X | _ | _ | _ | 2542.4 | Water | 89.0909 | 5.556 | 571.8944 | 3.88 |  | 54516.358 |  |  | 1 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1227 |  |  | X | _ | _ | _ | 2619.58 | Water | 94.7727 | 5.556 | 608.3672 | 3.88 |  | 50237.902 |  |  | 1 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1228 |  |  | X | _ | _ | _ | 2646.82 | Water | 103.6364 | 5.556 | 665.2649 | 3.88 |  | 54516.358 |  |  | 1 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1229 |  |  | X | _ | _ | _ | 3173.46 | Water | 92.5 | 5.556 | 593.7781 | 3.88 |  | 54652.182 |  |  | 1 |  |  |  | 11.1855 |  |  | _ | [13 empty] | _
1230 |  |  | X | _ | _ | _ | 3182.54 | Water | 102.0455 | 5.556 | 655.0525 | 3.88 |  | 60203.988 |  |  | 1 |  |  |  | 14.914 |  |  | _ | [13 empty] | _
1231 |  |  | X | _ | _ | _ | 3187.08 | Water | 110 | 5.556 | 706.1145 | 3.88 |  | 64805.026 |  |  | 1 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1232 |  |  | X | _ | _ | _ | 3196.16 | Water | 116.8182 | 5.556 | 749.8819 | 3.88 |  | 68845.79 |  |  | 1 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1233 |  |  | X | _ | _ | _ | 3291.5 | Water | 120.2273 | 5.556 | 771.7656 | 3.88 |  | 64329.642 |  |  | 1 |  |  |  | 18.6425 |  |  | _ | [13 empty] | _
1234 |  |  | X | _ | _ | _ | 3300.58 | Water | 125.9091 | 5.556 | 808.2385 | 3.88 |  | 68387.384 |  |  | 1 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1235 |  |  | X | _ | _ | _ | 3414.08 | Water | 134.7727 | 5.556 | 865.1361 | 3.88 |  | 68098.758 |  |  | 1 |  |  |  | 22.371 |  |  | _ | [13 empty] | _
1236 |  |  | X | 1555 | 2045 | 3515 | 1150 | Water | 31.2 | 5 | 180.1005 | 5 |  | 15600 |  |  | 1 | 1000 |  |  | 0.7457
1237 |  |  | X | 1755 | 2045 | 3515 | 1320 | Water | 39 | 5 | 225.1256 | 5 |  | 19800 |  |  | 1 | 1000 |  |  | 0.7457
1238 |  |  | X | 1955 | 2145 | 3625 | 1520 | Water | 46.8 | 5 | 270.1508 | 5 |  | 25200 |  |  | 1 | 1200 |  |  | 1.1185
1239 |  |  | X | 2155 | 2145 | 3625 | 1780 | Water | 54.6 | 5 | 315.1759 | 5 |  | 27000 |  |  | 1 | 1200 |  |  | 1.1185
1240 |  |  | X | 1555 | 2680 | 3670 | 1940 | Water | 62.4 | 5 | 360.201 | 5 |  | 33600 |  |  | 1 | 1200 |  |  | 1.4914
1241 |  |  | X | 1755 | 2680 | 3670 | 2050 | Water | 78 | 5 | 450.2513 | 5 |  | 42000 |  |  | 1 | 1300 |  |  | 1.4914
1242 |  |  | X | 1955 | 2880 | 3660 | 2220 | Water | 97.5 | 5 | 562.8141 | 5 |  | 50400 |  |  | 1 | 1500 |  |  | 3.7285
1243 |  |  | X | 2155 | 2880 | 3710 | 2320 | Water | 117 | 5 | 675.3769 | 5 |  | 59700 |  |  | 1 | 1500 |  |  | 3.7285
1244 |  |  | X | 2360 | 3080 | 3710 | 2670 | Water | 136.5 | 5 | 787.9397 | 5 |  | 68100 |  |  | 1 | 1700 |  |  | 5.5928
1245 |  |  | X | 2560 | 3180 | 3730 | 2830 | Water | 156 | 5 | 900.5025 | 5 |  | 80400 |  |  | 1 | 1800 |  |  | 5.5928
1246 |  |  | X | 2660 | 3380 | 3730 | 3170 | Water | 175.5 | 5 | 1013.0653 | 5 |  | 92400 |  |  | 1 | 2000 |  |  | 5.5928
1247 |  |  | X | 2960 | 3380 | 3730 | 3370 | Water | 195 | 5 | 1125.6281 | 5 |  | 101400 |  |  | 1 | 2000 |  |  | 7.457
1248 |  |  | X | 2960 | 2045 | 3515 | 2200 | Water | 62.4 | 5 | 360.201 | 5 |  | 31200 |  |  | 2 | 1000 |  |  | 1.4914
1249 |  |  | X | 3360 | 2045 | 3515 | 2540 | Water | 78 | 5 | 450.2513 | 5 |  | 39600 |  |  | 2 | 1000 |  |  | 1.4914
1250 |  |  | X | 3360 | 2680 | 3670 | 4000 | Water | 156 | 5 | 900.5025 | 5 |  | 84000 |  |  | 2 | 1300 |  |  | 2.9828
1251 |  |  | X | 900 | 600 | 1980 | 196 | Water | 9.0909 | 4.167 | 43.9847 | 3.889 |  | 4244.5 |  |  | 1 | 450 |  | 1400 | 0.37285
1252 |  |  | X | 900 | 900 | 1980 | 269 | Water | 13.6364 | 4.167 | 65.977 | 3.889 |  | 6451.64 |  |  | 1 | 700 |  | 1400 | 0.7457
1253 |  |  | X | 1200 | 900 | 1980 | 344 | Water | 18.1818 | 4.167 | 87.9693 | 3.889 |  | 8489 |  |  | 1 | 700 |  | 1400 | 1.1185
1254 |  |  | X | 1200 | 1200 | 1980 | 437 | Water | 22.7273 | 4.167 | 109.9617 | 3.889 |  | 11511.084 |  |  | 1 | 700 |  | 1400 | 1.1185
1255 |  |  | X | 1350 | 1200 | 1980 | 499 | Water | 27.2727 | 4.167 | 131.954 | 3.889 |  | 12733.5 |  |  | 1 | 700 |  | 1400 | 1.4914
1256 |  |  | X | 1500 | 1200 | 1980 | 610 | Water | 31.8182 | 4.167 | 153.9463 | 3.889 |  | 14176.63 |  |  | 1 | 700 |  | 1400 | 1.4914
1257 |  |  | X | 1500 | 1500 | 1980 | 663 | Water | 36.3636 | 4.167 | 175.9386 | 3.889 |  | 17826.9 |  |  | 1 | 700 |  | 1400 | 1.4914
1258 |  |  | X | 1800 | 1500 | 2440 | 788 | Water | 45.4545 | 4.167 | 219.9233 | 3.889 |  | 21392.28 |  |  | 1 | 900 |  | 960 | 2.2371
1259 |  |  | X | 1800 | 1800 | 2440 | 947 | Water | 54.5455 | 4.167 | 263.908 | 3.889 |  | 25636.78 |  |  | 1 | 900 |  | 960 | 2.2371
1260 |  |  | X | 1800 | 2100 | 2440 | 1102 | Water | 63.6364 | 4.167 | 307.8926 | 3.889 |  | 29881.28 |  |  | 1 | 900 |  | 960 | 2.2371
1261 |  |  | X | 2400 | 1800 | 2440 | 1241 | Water | 72.7273 | 4.167 | 351.8773 | 3.889 |  | 34125.78 |  |  | 1 | 1000 |  | 960 | 3.7285
1262 |  |  | X | 2400 | 2100 | 2440 | 1472 | Water | 86.3636 | 4.167 | 417.8543 | 3.889 |  | 39813.41 |  |  | 1 | 1000 |  | 960 | 3.7285
1263 |  |  | X | 2400 | 2250 | 2440 | 1518 | Water | 90.9091 | 4.167 | 439.8466 | 3.889 |  | 42614.78 |  |  | 1 | 1000 |  | 960 | 3.7285
1264 |  |  | X | 2400 | 2700 | 2670 | 1792 | Water | 109.0909 | 4.167 | 527.8159 | 3.889 |  | 51188.67 |  |  | 1 | 1200 |  | 960 | 5.5928
1265 |  |  | X | 3000 | 2400 | 2670 | 1991 | Water | 122.7273 | 4.167 | 593.7929 | 3.889 |  | 56876.3 |  |  | 1 | 1200 |  | 960 | 5.5928
1266 |  |  | X | 3000 | 2700 | 2670 | 2245 | Water | 136.3636 | 4.167 | 659.7699 | 3.889 |  | 64007.06 |  |  | 1 | 1200 |  | 960 | 5.5928
1267 |  |  | X | 3000 | 3000 | 2440 | 2400 | Water | 150 | 4.167 | 725.7469 | 3.889 |  | 71137.82 |  |  | 2 | 1000 |  | 960 | 7.457
1268 |  |  | X | 3000 | 3150 | 2440 | 2575 | Water | 159.0909 | 4.167 | 769.7315 | 3.889 |  | 74703.2 |  |  | 2 | 1000 |  | 960 | 7.457
1269 |  |  | X | 3000 | 3600 | 2440 | 2967 | Water | 181.8182 | 4.167 | 879.6932 | 3.889 |  | 85229.56 |  |  | 2 | 1000 |  | 960 | 7.457
1270 |  |  | X | 3600 | 3300 | 2670 | 3215 | Water | 200 | 4.167 | 967.6625 | 3.889 |  | 93718.56 |  |  | 2 | 1200 |  | 960 | 11.1855
1271 |  |  | X | 3600 | 3600 | 2670 | 3500 | Water | 218.1818 | 4.167 | 1055.6318 | 3.889 |  | 102377.34 |  |  | 2 | 1200 |  | 960 | 11.1855
1272 |  |  | X | 3600 | 3750 | 2670 | 3613 | Water | 227.2727 | 4.167 | 1099.6165 | 3.889 |  | 106621.84 |  |  | 2 | 1200 |  | 960 | 11.1855
1273 |  |  | X | 3600 | 4200 | 2670 | 3732 | Water | 254.5455 | 4.167 | 1231.5705 | 3.889 |  | 119355.34 |  |  | 2 | 1200 |  | 960 | 11.1855
1274 |  |  | X | 3600 | 4500 | 2670 | 4326 | Water | 272.7273 | 4.167 | 1319.5398 | 3.889 |  | 128014.12 |  |  | 2 | 1200 |  | 960 | 11.1855
1275 |  |  | X | 4500 | 4200 | 2670 | 5164 | Water | 318.1818 | 4.167 | 1539.4631 | 3.889 |  | 149236.62 |  |  | 3 | 1200 |  | 960 | 16.7782
1276 |  |  | X | 4500 | 4500 | 2670 | 5425 | Water | 340.9091 | 4.167 | 1649.4247 | 3.889 |  | 159932.76 |  |  | 3 | 1200 |  | 960 | 16.7782
1277 |  |  | X | 4500 | 4800 | 2670 | 5790 | Water | 363.6364 | 4.167 | 1759.3864 | 3.889 |  | 170628.9 |  |  | 3 | 1200 |  | 960 | 16.7782
1278 |  |  | X | 5400 | 4200 | 2670 | 5957 | Water | 381.8182 | 4.167 | 1847.3557 | 3.889 |  | 178778.34 |  |  | 3 | 1200 |  | 960 | 16.7782
1279 |  |  | X | 5400 | 4500 | 2670 | 6450 | Water | 409.0909 | 4.167 | 1979.3097 | 3.889 |  | 192021.18 |  |  | 3 | 1200 |  | 960 | 16.7782
1280 |  |  | X | 600 | 600 | 2590 | 165 | Water | 4.5455 | 4.167 | 21.9923 | 3.889 |  | 2843.815 |  |  | 1 | 450 |  | 1400 | 0.37285
1281 |  |  | X | 900 | 600 | 2590 | 185 | Water | 9.0909 | 4.167 | 43.9847 | 3.889 |  | 4244.5 |  |  | 1 | 450 |  | 1400 | 0.37285
1282 |  |  | X | 900 | 900 | 2590 | 250 | Water | 13.6364 | 4.167 | 65.977 | 3.889 |  | 6451.64 |  |  | 1 | 700 |  | 1400 | 0.7457
1283 |  |  | X | 1200 | 900 | 2590 | 325 | Water | 18.1818 | 4.167 | 87.9693 | 3.889 |  | 8489 |  |  | 1 | 700 |  | 1400 | 1.1185
1284 |  |  | X | 1200 | 1200 | 2590 | 415 | Water | 22.7273 | 4.167 | 109.9617 | 3.889 |  | 11511.084 |  |  | 1 | 700 |  | 1400 | 1.1185
1285 |  |  | X | 1350 | 1200 | 2590 | 475 | Water | 27.2727 | 4.167 | 131.954 | 3.889 |  | 12733.5 |  |  | 1 | 700 |  | 1400 | 1.4914
1286 |  |  | X | 1500 | 1200 | 2590 | 520 | Water | 31.8182 | 4.167 | 153.9463 | 3.889 |  | 14176.63 |  |  | 1 | 700 |  | 1400 | 1.4914
1287 |  |  | X | 1500 | 1500 | 2590 | 630 | Water | 36.3636 | 4.167 | 175.9386 | 3.889 |  | 17826.9 |  |  | 1 | 700 |  | 1400 | 1.4914
1288 |  |  | X | 1800 | 1500 | 3050 | 750 | Water | 45.4545 | 4.167 | 219.9233 | 3.889 |  | 21392.28 |  |  | 1 | 900 |  | 960 | 2.2371
1289 |  |  | X | 1800 | 1800 | 3050 | 900 | Water | 54.5455 | 4.167 | 263.908 | 3.889 |  | 25636.78 |  |  | 1 | 900 |  | 960 | 2.2371
1290 |  |  | X | 1800 | 2100 | 3050 | 1050 | Water | 63.6364 | 4.167 | 307.8926 | 3.889 |  | 29881.28 |  |  | 1 | 900 |  | 960 | 2.2371
1291 |  |  | X | 2400 | 1800 | 3050 | 1180 | Water | 72.7273 | 4.167 | 351.8773 | 3.889 |  | 34125.78 |  |  | 1 | 1000 |  | 960 | 3.7285
1292 |  |  | X | 2400 | 2100 | 3050 | 1300 | Water | 86.3636 | 4.167 | 417.8543 | 3.889 |  | 39813.41 |  |  | 1 | 1000 |  | 960 | 3.7285
1293 |  |  | X | 2400 | 2250 | 3050 | 1440 | Water | 90.9091 | 4.167 | 439.8466 | 3.889 |  | 42614.78 |  |  | 1 | 1000 |  | 960 | 3.7285
1294 |  |  | X | 2400 | 2700 | 3050 | 1720 | Water | 109.0909 | 4.167 | 527.8159 | 3.889 |  | 51188.67 |  |  | 1 | 1200 |  | 960 | 5.5928
1295 |  |  | X | 3000 | 2400 | 3050 | 1890 | Water | 122.7273 | 4.167 | 593.7929 | 3.889 |  | 56876.3 |  |  | 1 | 1200 |  | 960 | 5.5928
1296 |  |  | X | 3000 | 2700 | 3050 | 2130 | Water | 136.3636 | 4.167 | 659.7699 | 3.889 |  | 64007.06 |  |  | 1 | 1500 |  | 960 | 5.5928
1297 |  |  | X | 3000 | 3000 | 3050 | 2200 | Water | 150 | 4.167 | 725.7469 | 3.889 |  | 71137.82 |  |  | 1 | 1800 |  | 720 | 5.5928
1298 |  |  | X | 3000 | 3150 | 3050 | 2450 | Water | 159.0909 | 4.167 | 769.7315 | 3.889 |  | 74703.2 |  |  | 1 | 1800 |  | 720 | 5.5928
1299 |  |  | X | 3000 | 3600 | 3155 | 2820 | Water | 181.8182 | 4.167 | 879.6932 | 3.889 |  | 85229.56 |  |  | 1 | 1800 |  | 720 | 7.457
1300 |  |  | X | 3600 | 3300 | 3385 | 2967 | Water | 200 | 4.167 | 967.6625 | 3.889 |  | 93718.56 |  |  | 2 | 1200 |  | 960 | 11.1855
1301 |  |  | X | 3600 | 3600 | 3385 | 3200 | Water | 218.1818 | 4.167 | 1055.6318 | 3.889 |  | 102377.34 |  |  | 2 | 1200 |  | 960 | 11.1855
1302 |  |  | X | 3600 | 3750 | 3385 | 3430 | Water | 227.2727 | 4.167 | 1099.6165 | 3.889 |  | 106621.84 |  |  | 2 | 1200 |  | 960 | 11.1855
1303 |  |  | X | 3600 | 4200 | 3385 | 3840 | Water | 254.5455 | 4.167 | 1231.5705 | 3.889 |  | 119355.34 |  |  | 2 | 1200 |  | 960 | 11.1855
1304 |  |  | X | 3600 | 4500 | 3385 | 4110 | Water | 272.7273 | 4.167 | 1319.5398 | 3.889 |  | 128014.12 |  |  | 2 | 1500 |  | 960 | 11.1855
1305 |  |  | X | 4200 | 4200 | 3385 | 4870 | Water | 295.4545 | 4.167 | 1429.5014 | 3.889 |  | 139219.6 |  |  | 2 | 1800 |  | 720 | 11.1855
1306 |  |  | X | 4500 | 4200 | 3385 | 4900 | Water | 318.1818 | 4.167 | 1539.4631 | 3.889 |  | 149236.62 |  |  | 2 | 1800 |  | 720 | 11.1855
1307 |  |  | X | 4500 | 4500 | 3385 | 5100 | Water | 340.9091 | 4.167 | 1649.4247 | 3.889 |  | 159762.98 |  |  | 2 | 1800 |  | 720 | 11.1855
1308 |  |  | X | 4800 | 4500 | 3385 | 5330 | Water | 363.6364 | 4.167 | 1759.3864 | 3.889 |  | 170459.12 |  |  | 2 | 1800 |  | 720 | 14.914
1309 |  |  | X | 5400 | 4200 | 3385 | 5660 | Water | 381.8182 | 4.167 | 1847.3557 | 3.889 |  | 178778.34 |  |  | 2 | 1900 |  | 720 | 14.914
1310 |  |  | X | 5400 | 4500 | 3385 | 6150 | Water | 409.0909 | 4.167 | 1979.3097 | 3.889 |  | 191851.4 |  |  | 2 | 1900 |  | 720 | 14.914